## Index & Read Me
WORKBOOK GUIDE · INDEX & READ ME
Data Center Template, Northern Virginia — 90 MW Tier III hyperscale data center. Owner-side cost estimate + capital-program controls toolkit. Independent, illustrative model — not affiliated with any actual named project.
TOTAL CAMPUS INVESTMENT | IT CAPACITY · COST / MW · GROSS AREA · TABS
1088341827.0674 | 90 MW · $12.1M / MW · 800,000 SF · 39 sheets
EXECUTIVE & QA
Dashboard | Executive summary — headline KPIs, five cost charts, six QC tie checks, and live delivery metrics (EVM / risk / procurement).
Basis of Estimate | Methodology, inclusions / exclusions, key assumptions, and the scenario-control & value-engineering notes.
COST ESTIMATE
Construction Budget | The estimate spine — 25 CSI divisions, ~400 line items building to the $1.09B grand total.
Unit Cost Database | Standard reference unit pricing; the active pricing tier (set on Scenario & Presets) drives the estimate.
Location Factors | Regional cost-adjustment factors for the Loudoun County, VA market.
Allowances & Alternates | Carried allowances and priced add/deduct alternates.
CSA Summary | Civil / structural / architectural scope breakout.
Variance Tracker | Estimate vs. subcontractor pricing by division.
Client Proposal | Client-facing cost summary (Turner & Townsend format).
CAMPUS & PROGRAM
Campus Rollup | Per-building + shared-infrastructure rollup to the campus total; the hub every other tab references.
Phased Capital Plan | Six-building sequential deployment; Phase 1 reconciles exactly to this estimate, then escalates to build-out.
Milestone Tracker | Estimate evolution across design milestones (Concept → SD → DD → CD → GMP).
DELIVERY CONTROLS
Cash Flow & EVM | Earned-value S-curve with SPI / CPI, EAC / ETC, and PV reconciliation to budget at completion.
Draw Schedule | 30-month construction draw / cash-flow schedule.
Risk & Contingency | Risk register, analytical P50 / P80 / P90, and a 10,000-iteration Monte Carlo vs. the carried contingency.
Change Order Log | Change orders with type / status / funding and a running contingency drawdown.
Procurement & Long-Lead | Equipment lead times, back-calculated order-by dates, and escalation exposure with late-order flags.
Construction Schedule | Cradle-to-grave CPM master schedule — WBS, dependency-linked dates, critical path & month-by-month Gantt; NTP tied to Construction Budget start.
Schedule Acceleration | Scenario model to recover schedule toward the Q3-2028 target — acceleration levers with day-savings, cost premium & risk.
DECISION SUPPORT
Scenario & Presets | Control panel — pricing tier, cooling technology, resiliency tier, redundancy, and density presets that drive the whole model.
Scenario Comparison | The live scenario beside three saved snapshots with $/MW deltas.
Value Engineering | VE log with accept / reject decisions and a live VE-adjusted total.
Bid Leveling | Price normalization across bidders for a single package.
Bid Evaluation | Weighted CMAR / GMP scoring across six criteria with an auto recommendation.
GC Bid Form | Print-ready general-contractor bid form — 24 CSI divisions, alternates, unit prices, schedule, quals & signature; prices feed Bid Leveling.
Bid Cover Sheet | Sealed-bid cover sheet / envelope label with required-documents checklist; auto-fills from the GC Bid Form.
Power & Space Capacity | IT-load-driven electrical / cooling / space sizing, binding-constraint, and stranded-capacity analysis.
Carbon & Sustainability | Embodied + operational carbon vs. capex, with decarbonization levers.
TCO 8-Year | Eight-year total-cost-of-ownership model.
OWNER ECONOMICS
Total Development Cost | All-in owner budget — construction plus land, utility, owner PM/soft costs, financing (IDC) and contingency.
Investment Pro Forma | NNN lease-up pro forma — unlevered IRR, NPV, yield-on-cost and a lease-rate x exit-cap sensitivity.
Variance-to-Return | Translates cost variance (EVM forecast + bids) into IRR, yield-on-cost and NPV impact.
IC Summary | One-page committee view — capitalization, levered + unlevered returns, key risks and recommendation.
Sources & Uses | Reconciles capital required (Uses = TDC) against funding (Sources = senior debt + sponsor equity).
Capital Stack & Returns | Sizes permanent debt to the binding covenant; levered equity IRR, multiple, cash-on-cash and DSCR.
REFERENCE
Benchmark Library | Three-source $/MW benchmark set (T&T DCCI, Mortenson, CBRE).
Reference Models | Comparable reference projects.
HOW TO USE
• | Yellow cells are inputs; everything else is a live formula. Blue underlined names above jump to that sheet.
• | Drive the model from Scenario & Presets — pricing tier and cooling technology flow through every dependent tab automatically.
• | Six QC ties on the Dashboard confirm the workbook stays internally reconciled; they should all read “✅ Tie.”
• | Analysis tabs (EVM actuals, risk, procurement, capacity, carbon, bids, change orders, phasing) carry illustrative inputs that recalculate when real project data is entered.

## Dashboard
DATA CENTER CAMPUS
Data Center Template, Northern Virginia — Cost Estimate
Prepared for Confidential Hyperscaler ¦ Loudoun County, VA ¦ Class 3 (DD) Estimate (−20% / +30%) ¦ May 1, 2026
TIER 1 · INVESTMENT & RETURNS
DEVELOPMENT COST (ALL-IN) |  |  | SPONSOR EQUITY |  | LEVERED EQUITY IRR |  | EQUITY MULTIPLE (LEV.)
1512873780.308 |  |  | 605149512.1232 |  | 26.65% |  | 5.1974
UNLEVERED IRR |  |  | STABILIZED YIELD-ON-COST |  | STABILIZED DSCR |  | DEVELOPMENT MARGIN
17.44% |  |  | 10.9% |  | 2.3726 |  | 67.71%
Levered to sponsor equity — figures link live to Capital Stack & Returns, Investment Pro Forma and Sources & Uses.
TIER 2 · COST & BENCHMARKING
TOTAL CAMPUS INVESTMENT |  |  | IT CAPACITY |  | COST PER MW |  | GROSS BUILT AREA
$1.09B |  |  | 90.0 MW |  | $12.1M |  | 800K SF
Across 3 buildings + shared infrastructure |  |  | Total IT load delivered |  | ▲ Above industry median |  | $1,360 / SF blended
Note: Development Cost (All-In) of $1,513M is the full owner budget (TDC) = Total Campus Investment / construction $1,088M + owner soft costs $269M + financing/IDC $84M + owner's contingency $72M. See Total Development Cost tab.
DESIGN SCENARIOS — CAMPUS COST BY CONFIGURATION (90 MW / 800K SF) | [5 empty] | COST EVOLUTION BY DESIGN MILESTONE
Design Scenario | CSA | MEP | Cx / GC / Soft | Total | $ / MW
Current (live) — Base | 275731915.8661 | 609160998.0974 | 203448913.1039 | 1088341827.0674 | 12092686.9674
Reference — Hyperscale (Hybrid) | 416840508.0361 | 1080845097 | 260549900.1627 | 1758235505.1988 | 19535950.0578
Air-Cooled (Chilled Water) | 416840508.0361 | 1002231672 | 257685855.8631 | 1676758035.8992 | 18630644.8433
AI / HPC — Liquid Cooled | 618530193.4411 | 2069717493 | 331039337.1735 | 3019287023.6146 | 33547633.5957
Enterprise | 416840508.0361 | 1180628910 | 257685855.8631 | 1855155273.8992 | 20612836.3767
Colocation | 416840508.0361 | 952120088 | 257685855.8631 | 1626646451.8992 | 18073849.4655
Edge | 275731915.8661 | 578065774 | 204656062.1505 | 1058453752.0167 | 11760597.2446
Typical (industry median) | — | — | — | 1026000000 | 11400000
All design scenarios are modeled (linked to Scenario Comparison). Enterprise & Colocation share Air-Cooled's Mid · Chilled-Water cost — they differ only in tier / redundancy / density, which don't drive cost in this estimate. Typical = industry median $/MW × 90 MW.
BENCHMARK POSITIONING | [5 empty] | INVESTMENT BY DISCIPLINE
CURRENT ESTIMATE — $/MW
$12.09M |  |  | INDUSTRY MEDIAN
$11.4M / MW
▲ $0.7M / MW above median (+6.1%)
Range across 10 comparable Tier III projects: $9.8M – $17.8M / MW
LOWEST COMPARABLE |  | MEDIAN COMPARABLE |  | HIGHEST COMPARABLE
$9.8M / MW |  | $11.4M / MW |  | $17.8M / MW
TIER 3 · DELIVERY & CONTROLS
KEY HIGHLIGHTS
◆ ESTIMATE CONFIDENCE |  |  | ◆ VALUE ENGINEERING |  |  | ◆ TENDER READINESS
Class 3 (DD) |  |  | $68,805,864 identified |  |  | Ready to bid
Accuracy band −20% / +30%. Estimate built up from CSI-level detail across all 19 divisions, anchored against benchmark library of 10 comparable Tier III projects. |  |  | Active scenario: Balanced — $35,305,864 adopted (3.2% of base) → $11,700,400/MW. |  |  | Bid packages and tender documents prepared. Subcontractor outreach underway across structural, MEP, and specialty trades.
QC CHECKS
Construction Budget total = Campus Rollup total |  |  |  |  | ✅ Tie | ◆ SCOPE ADDS — ALLOWANCES & ALTERNATES
Client Proposal subtotal = sum of divisions |  |  |  |  | ✅ Tie | 17550000
CSA Summary total = Campus Rollup CSA |  |  |  |  | ✅ Tie
Draw Schedule total = Construction Budget |  |  |  |  | ✅ Tie | Allowances $17,550,000 · Accepted alternates $0
TCO sensitivity center = 8-yr TCO |  |  |  |  | ✅ Tie | Flows to Client Proposal total: $1.11B
Cash Flow PV curve = Budget at Completion (BAC) |  |  |  |  | ✅ Tie
Construction Budget ties to Unit Cost Database |  |  |  |  | ✅ Tie
PROJECT CONTROLS — DELIVERY METRICS
◆ SCHEDULE & COST (EVM) |  |  | ◆ RISK-BASED CONTINGENCY |  |  | ◆ LONG-LEAD PROCUREMENT
SPI — · CPI — |  |  | $120,754,987 P80 |  |  | 5 pkgs overdue to order
○ Not started · ○ Not started (data date: month 0) |  |  | P80 vs $98,940,166 carried at flat 10% — exceeds allowance. |  |  | $1087M tracked · $30.3M escalation exposure if delayed.
SCENARIO MODELING
Active configuration drives the live estimate — set on Scenario & Presets, compared on Scenario Comparison. Current preset: Hyperscale
◆ ACTIVE CONFIGURATION |  |  | ◆ LIVE SCENARIO IMPACT |  |  | ◆ MODELED RANGE
Liquid-Cooled (DLC) |  |  | 12092686.9674 |  |  | $12.1M – $33.5M / MW
Pricing tier: Low |  |  | Estimate total: $1.09B |  |  | Total: $1.09B – $3.02B
Tier III · N+1 · High (15–30 kW) |  |  | ● Within archetype band |  |  | Current vs baseline: -38.1% (-$670M)
TIER 4 · SCENARIO & COST BACK-UP
SCENARIO COMPARISON — LIVE vs SAVED SNAPSHOTS
Scenario |  | Cooling Technology |  | Total Estimate |  | $ / MW |  | Δ vs Baseline
Current (live) |  | Liquid-Cooled (DLC) |  | 1088341827.0674 |  | 12092686.9674 |  | -38.1%
Reference — Hyperscale (Hybrid) |  | Hybrid (As-Designed) |  | 1758235505.1988 |  | 19535950.0578 |  | 0%
Air-Cooled (Chilled Water) |  | Chilled Water (Air-Cooled) |  | 1676758035.8992 |  | 18630644.8433 |  | -4.634%
AI / HPC — Liquid Cooled |  | Liquid-Cooled (DLC) |  | 3019287023.6146 |  | 33547633.5957 |  | 71.72%
Enterprise |  | Chilled Water (Air-Cooled) |  | 1855155273.8992 |  | 20612836.3767 |  | 5.512%
Colocation |  | Chilled Water (Air-Cooled) |  | 1626646451.8992 |  | 18073849.4655 |  | -7.484%
Edge |  | Chilled Water (Air-Cooled) |  | 1058453752.0167 |  | 11760597.2446 |  | -39.8%
Snapshots C–E are saved on the Scenario Comparison tab; re-capture after model edits. Live row reflects the current Scenario & Presets configuration.
COST ANALYSIS
Cost breakdown by trade, capital by building, and unit cost vs. industry benchmark.
CONSTRUCTION SCHEDULE
Milestone completion dates across the build program — design through commissioning.
TIER 5 · ENGINEERING, ESG & PROGRAM DELIVERY
◆ INVESTMENT COMMITTEE |  |  | ◆ DELIVERABLE CAPACITY |  |  | ◆ CHANGE ORDERS & CONTINGENCY
ACCEPT |  |  | 89.7 MW usable |  |  | $19.5M drawn
Levered IRR 26.7% · 5.20x multiple · Unlevered 17.4% |  |  | Binding: standby generation · 99.7% of design |  |  | $79.4M of $98.9M remaining (80%)
Stabilized value $2.54B · dev. profit $1,024M |  |  | 10.3 MW stranded · 135,000 SF white space |  |  | ● Healthy — over half of contingency remains
◆ LIFECYCLE CARBON |  |  | ◆ PHASED CAMPUS BUILD-OUT |  |  | ◆ SCHEDULE RECOVERY
0.68M tCO₂e |  |  | $1.98B program |  |  | 147 days recovered
0.85 tCO₂e/SF · 58% embodied · Efficient scenario |  |  | 180 MW at build-out · $11.0M/MW blended |  |  | $17.8M premium · $120,748/day
Water 126 ML/yr · −71% achievable with levers |  |  | Phase 1 $1.09B (ties to estimate) · expansion $894M |  |  | ✓ YES — meets Q3 2028
◆ ESTIMATE vs SUBCONTRACTOR BIDS |  |  | All Tier 5 figures link live to their source tabs; values refresh automatically when the model changes.
Awaiting bids
Budget $1.09B across 24 CSI divisions — sub bids plug into the tracker as received.
PROGRAM CONTROLS — CONTINGENCY & PHASED BUILD-OUT
Contingency balance vs. monitor/critical thresholds (Change Order Log) · cumulative capex and blended $/MW across the 6-building campus (Phased Capital Plan)
Note on F36: Kevin: Industry median $/MW (Benchmark Library) × 90 MW. Reference benchmark, not a project estimate.

## Scenario & Presets
SCENARIO & PRESETS — PROJECT CONFIGURATION
Pick an archetype preset for guidance, then set the active configuration. Pricing Tier and Cooling Technology drive the live estimate.
1 · PROJECT ARCHETYPE PRESET
Select Archetype: | Hyperscale
Recommended configuration
Resiliency Tier: | Tier III
Redundancy: | N+1
Rack Density: | High (15–30 kW)
Cooling Technology: | Hybrid (As-Designed)
Pricing Tier: | Mid
Expected $/MW band: | $9.5M – $14.0M / MW
2 · ACTIVE CONFIGURATION (drives the live model)
Pricing Tier: | Low | → sets every unit cost (Unit Cost Database)
Cooling Technology: | Liquid-Cooled (DLC) | → toggles Division 23 cooling scope (air / chilled-water / liquid)
Resiliency Tier: | Tier III | → documentation & benchmark context
Redundancy: | N+1 | → drives MEP via redundancy factor (critical power)
Rack Density: | High (15–30 kW) | → drives MEP via rack-density factor
3 · LIVE SCENARIO IMPACT
Estimate Total: | 1088341827.0674
Cost per MW: | 12092686.9674
Selected-archetype band: | $9.5M – $14.0M / MW
Position vs archetype band: | ● Within archetype band
REFERENCE TABLES — used by the dropdowns above. Do not edit.
Archetype | Tier | Redundancy | Rack Density | Cooling Technology | Pricing | $/MW Low | $/MW High
Hyperscale | Tier III | N+1 | High (15–30 kW) | Hybrid (As-Designed) | Mid | 9.5 | 14
Enterprise | Tier III+ | 2N | Medium (8–15 kW) | Chilled Water (Air-Cooled) | Mid | 11 | 16
Colocation | Tier III | N+1 | Medium (8–15 kW) | Chilled Water (Air-Cooled) | Mid | 10 | 15
Edge | Tier II | N+1 | Low (≤8 kW) | Chilled Water (Air-Cooled) | Low | 8 | 13
AI / HPC | Tier III+ | 2N | Ultra (30+ kW) | Liquid-Cooled (DLC) | High | 14 | 22
COOLING TECHNOLOGY FACTORS (× Division 23 scope)
Technology | Air-side | Chilled-water | Liquid
Hybrid (As-Designed) | 1 | 1 | 1
Chilled Water (Air-Cooled) | 1 | 1 | 0
Liquid-Cooled (DLC) | 0.4 | 0.6 | 1
Full Immersion | 0.2 | 0.5 | 1.1
Active cooling factors → | 0.4 | 0.6 | 1
REDUNDANCY FACTORS (× critical-power train scope)
Redundancy | Factor
N | 0.85
N+1 | 1
2N | 1.8
2N+1 | 2
Active redundancy factor → | 1
RACK DENSITY FACTORS (× rack cooling & power scope)
Density | Factor
Low (≤8 kW) | 0.9
Medium (8–15 kW) | 0.95
High (15–30 kW) | 1
Ultra (30+ kW) | 1.15
Active density factor → | 1
Critical-power share of MEP | 0.3 | share of MEP that scales with redundancy (UPS/gen/distribution)
MEP redundancy multiplier | 1 | → applied to MEP
Active MEP config factor (× MEP) | 1 | redundancy × rack-density; N+1 & High = 1.00 (baseline)
Note on B67: MEP config factor = [(1-crit)+crit*redundancyFactor] * densityFactor. Wires the redundancy (B54) and density (B63) factors into MEP cost so resiliency/redundancy/density actually change the estimate. Source: model design, 2026.

## Scenario Comparison
SCENARIO COMPARISON
Column B is the recommended/live case. Reference columns reflect each archetype incl. redundancy & rack-density drivers.
★ RECOMMENDED
Configuration | Current (live) | Reference — Hyperscale (Hybrid) | Air-Cooled (Chilled Water) | AI / HPC — Liquid Cooled | Enterprise | Colocation | Edge
Pricing Tier | Low | Mid | Mid | High | Mid | Mid | Low
Cooling Technology | Liquid-Cooled (DLC) | Hybrid (As-Designed) | Chilled Water (Air-Cooled) | Liquid-Cooled (DLC) | Chilled Water (Air-Cooled) | Chilled Water (Air-Cooled) | Chilled Water (Air-Cooled)
Resiliency Tier | Tier III | Tier III | Tier III | Tier III+ | Tier III+ | Tier III | Tier II
Redundancy | N+1 | N+1 | N+1 | 2N | 2N | N+1 | N+1
Rack Density | High (15–30 kW) | High (15–30 kW) | High (15–30 kW) | Ultra (30+ kW) | Medium (8–15 kW) | Medium (8–15 kW) | Low (≤8 kW)
COST OUTCOMES
Total Estimate | 1088341827.0674 | 1758235505.1988 | 1676758035.8992 | 3019287023.6146 | 1855155273.8992 | 1626646451.8992 | 1058453752.0167
Cost per MW | 12092686.9674 | 19535950.0578 | 18630644.8433 | 33547633.5957 | 20612836.3767 | 18073849.4655 | 11760597.2446
CSA (Shell & Structure) | 275731915.8661 | 416840508.0361 | 416840508.0361 | 618530193.4411 | 416840508.0361 | 416840508.0361 | 275731915.8661
MEP (Mechanical / Electrical) | 609160998.0974 | 1080845097 | 1002231672 | 2069717493 | 1180628910 | 952120088 | 578065774
Other (Commissioning, GC, Soft) | 203448913.1039 | 260549900.1627 | 257685855.8631 | 331039337.1735 | 257685855.8631 | 257685855.8631 | 204656062.1505
COST vs BASELINE (baseline = Reference — Hyperscale)
Δ vs baseline ($) | -669893678.1314 | 0 | -81477469.2996 | 1261051518.4158 | 96919768.7004 | -131589053.2996 | -699781753.1821
Δ vs baseline (%) | -38.1% | 0% | -4.634% | 71.72% | 5.512% | -7.484% | -39.8%
$/MW vs median ($11.4M) | 692686.9674 | 8135950.0578 | 7230644.8433 | 22147633.5957 | 9212836.3767 | 6673849.4655 | 360597.2446
VALUE-ENGINEERING OVERLAY (recommended case)
Active VE Scenario | Balanced
VE Savings (adopted) | 35305864
VE-Adjusted Total | 1053035963.0674
VE-Adjusted $/MW | 11700399.5896
Each archetype now reflects its redundancy (2N vs N+1) and rack-density premium on MEP.
CARBON & SUSTAINABILITY
Lifecycle Carbon (tCO₂e) | 683824 | 2552332
Carbon Intensity (tCO₂e/SF) | 0.85478 | 3.1904
Annual Operational (tCO₂e/yr) | 18921.6 | 143488.8
Embodied Share (%) | 58.49% | 15.67%
Annual Water (ML/yr) | 126.144 | 1135.296
WUE (L/kWh) | 0.2 | 1.8
Carbon vs baseline (%) | -73.21%
Carbon is driven by cooling strategy. Recommended Liquid-DLC design maps to the Efficient profile; Hyperscale-Hybrid baseline maps to Base. Air-cooled options (D–H) share modeled cost but differ in PUE/WUE — see the Carbon & Sustainability tab to compare Efficient / Base / Conservative scenarios in full.
Note on F5: Kevin: Same pricing × cooling (Mid · Chilled Water) as the Air-Cooled scenario, so modeled cost is identical. Differs only in documented Tier/Redundancy/Density, which don't drive cost in this model.
Note on G5: Kevin: Same pricing × cooling (Mid · Chilled Water) as the Air-Cooled scenario, so modeled cost is identical. Differs only in documented Tier/Redundancy/Density, which don't drive cost in this model.

## Construction Budget
DATA CENTER CONSTRUCTION BUDGET
Project Name: |  | Data Center Template, Northern Virginia |  | Start Date: | 2026-05-01
Project Location: |  | Loudoun County, VA |  | Target Completion: | Q1 2029
Owner / Client: |  | Confidential Hyperscaler |  | Architect / Engineer: | HKS / Page Southerland Page
Total Facility Area (SF): |  | 800000 |  | Halls / Pods: | 9 halls (3 per building × 3 bldgs)
Tier Rating: |  | Tier III |  | Contingency %: | 10% | Escalation %: | 3.5%
Design PUE: |  | 1.4 |  |  |  | Location Factor: | 1
Total IT Load (MW): |  | 90 |  |  |  | Estimate Date: | 2026-05-01
UPS Capacity (MW): |  | 90
Generator Capacity (MW): |  | 112.5
Cooling Capacity (tons): |  | 25650
Raised Floor Area (SF): |  | 440000
Redundancy: |  | N+1
# | CSI Code | Description | Qty | Unit | Unit Cost ($) | Contingency % | Extended Cost ($) | Building | Scope
SOFT COSTS / PRE-CONSTRUCTION | [8 empty] | Soft
1 | SC 01 00 | Architectural & Engineering Design Fees | 90 | MW | 275000 | 10% | 28177875 | Shared | Soft
2 | SC 02 00 | MEP Engineering — Critical Systems Design | 90 | MW | 225000 | 10% | 23054625 | Shared | Soft
3 | SC 03 00 | Structural Engineering | 90 | MW | 65000 | 10% | 6660225 | Shared | Soft
4 | SC 04 00 | Civil Engineering & Survey | 90 | MW | 35000 | 10% | 3586275 | Shared | Soft
5 | SC 05 00 | Geotechnical Investigation | 3 | EA | 125000 | 10% | 426937.5 | Shared | Soft
6 | SC 06 00 | Environmental Consulting / Phase I ESA | 1 | LS | 250000 | 10% | 284625 | Shared | Soft
7 | SC 07 00 | Permitting & Entitlement Fees | 90 | MW | 85000 | 10% | 8709525 | Shared | Soft
8 | SC 08 00 | Utility Connection & Impact Fees | 90 | MW | 175000 | 10% | 17931375 | Shared | Soft
9 | SC 09 00 | Third-Party Commissioning Agent (CxA) | 90 | MW | 7500 | 10% | 768487.5 | Shared | Soft
10 | SC 10 00 | Uptime Institute Tier Certification | 1 | LS | 350000 | 10% | 398475 | Shared | Soft
11 | SC 11 00 | LEED / Sustainability Certification | 1 | LS | 250000 | 10% | 284625 | Shared | Soft
12 | SC 12 00 | Owner's Representative / PM Fees | 24 | MO | 95000 | 10% | 2595780 | Shared | Soft
13 | SC 13 00 | Legal & Contract Administration | 24 | MO | 25000 | 10% | 683100 | Shared | Soft
14 | SC 14 00 | Cost Estimating / QS Services | 24 | MO | 35000 | 10% | 956340 | Shared | Soft
15 | SC 15 00 | Building Information Modeling (BIM) | 90 | MW | 85000 | 10% | 8709525 | Shared | Soft
16 | SC 16 00 | Third-Party Testing & Inspection (IOR) | 24 | MO | 55000 | 10% | 1502820 | Shared | Soft
17 | SC 17 00 | FF&E — NOC / SOC / Office Fit-Out | 40000 | SF | 175 | 10% | 7969500 | Shared | Soft
18 | SC 18 00 | Move Management & Logistics | 1 | LS | 350000 | 10% | 398475 | Shared | Soft
|  | Subtotal — SOFT COSTS / PRE-CONSTRUCTION |  |  |  |  | 113098590
GENERAL CONDITIONS & REQUIREMENTS | [8 empty] | GC
1 | 01 10 00 | Project Management & Supervision | 24 | MO | 80000 | 10% | 2185920 | Shared | GC
2 | 01 20 00 | Price & Payment Procedures | 24 | MO | 17500 | 10% | 478170 | Shared | GC
3 | 01 30 00 | Administrative Requirements | 24 | MO | 12600 | 10% | 344282.4 | Shared | GC
4 | 01 31 00 | Project Management Software (Procore/Primavera) | 24 | MO | 5950 | 10% | 162577.8 | Shared | GC
5 | 01 40 00 | Quality Requirements — QA/QC Program | 24 | MO | 45500 | 10% | 1243242 | Shared | GC
6 | 01 50 00 | Temporary Facilities — Site Office, Laydown | 24 | MO | 20000 | 10% | 546480 | Shared | GC
7 | 01 50 10 | Temporary Utilities — Power, Water, Sanitary | 24 | MO | 24500 | 10% | 669438 | Shared | GC
8 | 01 51 00 | Temporary Construction — Fencing, Barriers | 24 | MO | 17500 | 10% | 478170 | Shared | GC
9 | 01 52 00 | Construction Waste Management & Recycling | 24 | MO | 24500 | 10% | 669438 | Shared | GC
10 | 01 54 00 | Construction Cleaning — Progress & Final | 24 | MO | 45500 | 10% | 1243242 | Shared | GC
11 | 01 55 00 | Vehicular Access & Haul Roads | 24 | MO | 12600 | 10% | 344282.4 | Shared | GC
12 | 01 56 00 | Environmental Protection | 24 | MO | 17500 | 10% | 478170 | Shared | GC
13 | 01 60 00 | Product Requirements — Submittals & Substitutions | 24 | MO | 12600 | 10% | 344282.4 | Shared | GC
14 | 01 70 00 | Execution & Closeout Requirements | 24 | MO | 17500 | 10% | 478170 | Shared | GC
15 | 01 73 00 | Permits, Fees & Inspections | 1 | LS | 4525263.9443 | 10% | 5152013.0006 | Shared | GC
16 | 01 74 00 | Bonds — Performance & Payment | 1 | LS | 10860633.4664 | 10% | 12364831.2015 | Shared | GC
17 | 01 76 00 | Insurance — Builder's Risk, Wrap-Up | 1 | LS | 13575791.833 | 10% | 15456039.0018 | Shared | GC
18 | 01 78 00 | Closeout Submittals — As-Builts, Warranties | 24 | MO | 12600 | 10% | 344282.4 | Shared | GC
|  | Subtotal — GENERAL CONDITIONS & REQUIREMENTS |  |  |  |  | 42983030.6039
COMMISSIONING & TESTING | [8 empty] | Cx
1 | CX 01 00 | Commissioning Management & Administration | 90 | MW | 50000 | 10% | 5123250 | All Buildings | Cx
2 | CX 02 00 | Level 1 Cx — Factory Witness Testing | 27 | MW | 35000 | 10% | 1075882.5 | All Buildings | Cx
3 | CX 03 00 | Level 2 Cx — Component Verification (Individual Equipment) | 45 | MW | 45000 | 10% | 2305462.5 | All Buildings | Cx
4 | CX 04 00 | Level 3 Cx — Subsystem Verification | 45 | MW | 55000 | 10% | 2817787.5 | All Buildings | Cx
5 | CX 05 00 | Level 4 Cx — System Verification (Integrated) | 90 | MW | 75000 | 10% | 7684875 | All Buildings | Cx
6 | CX 06 00 | Level 5 Cx — Integrated Systems Testing (IST) | 90 | MW | 75000 | 10% | 7684875 | All Buildings | Cx
7 | CX 07 00 | Performance Verification Testing | 90 | MW | 65000 | 10% | 6660225 | All Buildings | Cx
8 | CX 08 00 | Seasonal Testing — Summer / Winter Peaks | 27 | MW | 45000 | 10% | 1383277.5 | All Buildings | Cx
9 | CX 09 00 | Failure Mode & Effects Testing (FMEA) | 90 | MW | 35000 | 10% | 3586275 | All Buildings | Cx
10 | CX 10 00 | Documentation — O&M Manuals, As-Builts | 90 | MW | 25000 | 10% | 2561625 | All Buildings | Cx
11 | CX 11 00 | Staff Training — Critical Systems Operation | 90 | MW | 18000 | 10% | 1844370 | All Buildings | Cx
12 | CX 12 00 | Uptime Institute Tier Certification Support | 1 | LS | 250000 | 10% | 284625 | All Buildings | Cx
13 | CX 13 00 | Temporary Provisions — Load Banks for IST | 45 | MW | 35000 | 10% | 1793137.5 | All Buildings | Cx
14 | CX 14 00 | Deficiency Tracking & Remediation | 90 | MW | 25000 | 10% | 2561625 | All Buildings | Cx
|  | Subtotal — COMMISSIONING & TESTING |  |  |  |  | 47367292.5
DIVISION 03 — CONCRETE | [8 empty] | CSA
1 | 03 10 00 | Concrete Formwork — Foundations | 1185.1852 | CY | 220 | 10% | 296853.3333 | All Buildings | CSA
2 | 03 20 00 | Concrete Reinforcement — Rebar | 1185.1852 | CY | 240 | 10% | 323840 | All Buildings | CSA
3 | 03 30 00 | Cast-in-Place — Foundation Walls | 888.8889 | CY | 450 | 10% | 455400 | All Buildings | CSA
4 | 03 30 10 | Cast-in-Place — Equipment Pads (Generator, Chiller, Transformer) | 592.5926 | CY | 650 | 10% | 438533.3333 | All Buildings | CSA
5 | 03 30 20 | Cast-in-Place — Elevated Slabs — breakdown ↓ | 240000 | SF | 14 | 10% | 3825360 | All Buildings | CSA
| 3 30 21 | • Elevated Slabs — Concrete | 0 | LS | 1848000 | 10% | 0 | All Buildings | CSA
| 3 30 22 | • Elevated Slabs — Rebar | 0 | LS | 672000 | 10% | 0 | All Buildings | CSA
| 3 30 23 | • Elevated Slabs — Forming | 0 | LS | 504000 | 10% | 0 | All Buildings | CSA
| 3 30 24 | • Elevated Slabs — Finishing | 0 | LS | 336000 | 10% | 0 | All Buildings | CSA
6 | 03 30 30 | Cast-in-Place — Slab on Grade (Data Halls) — breakdown ↓ | 605548.2847 | SF | 10 | 10% | 6894167.2209 | All Buildings | CSA
| 3 30 31 | • Slab on Grade — Concrete | 0 | LS | 3330515.5656 | 10% | 0 | All Buildings | CSA
| 3 30 32 | • Slab on Grade — Reinforcement | 0 | LS | 1211096.5694 | 10% | 0 | All Buildings | CSA
| 3 30 33 | • Slab on Grade — Finishing & Curing | 0 | LS | 908322.427 | 10% | 0 | All Buildings | CSA
| 3 30 34 | • Slab on Grade — Vapor Barrier Prep | 0 | LS | 605548.2846 | 10% | 0 | All Buildings | CSA
7 | 03 30 40 | Cast-in-Place — Loading Dock / Ramps | 16000 | SF | 18 | 10% | 327888 | All Buildings | CSA
8 | 03 35 00 | Concrete Finishing — Data Hall Floor Flatness (FF/FL) | 440000 | SF | 2.8 | 10% | 1402632 | All Buildings | CSA
9 | 03 40 00 | Precast Concrete — Tilt-Up Panels — breakdown ↓ | 480000 | SF | 18 | 10% | 9836640 | All Buildings | CSA
| 3 40 01 | • Tilt-Up — Panel Fabrication | 0 | LS | 5184000 | 10% | 0 | All Buildings | CSA
| 3 40 02 | • Tilt-Up — Erection & Bracing | 0 | LS | 2160000 | 10% | 0 | All Buildings | CSA
| 3 40 03 | • Tilt-Up — Connections & Joints | 0 | LS | 864000 | 10% | 0 | All Buildings | CSA
| 3 40 04 | • Tilt-Up — Finishing | 0 | LS | 432000 | 10% | 0 | All Buildings | CSA
10 | 03 41 00 | Precast Structural Members | 40000 | SF | 21 | 10% | 956340 | All Buildings | CSA
11 | 03 05 00 | Concrete Accessories — Embeds, Anchors | 800000 | SF | 0.35 | 10% | 318780 | All Buildings | CSA
12 | 03 15 00 | Under-Slab Vapor Barrier & Joints | 600000 | SF | 1.1 | 10% | 751410 | All Buildings | CSA
13 | 03 30 70 | Concrete Testing & Inspection | 1 | LS | 180000 | 10% | 204930 | All Buildings | CSA
14 | 03 30 80 | Cast-in-Place — Mat Foundation / Raft — breakdown ↓ | 9500 | CY | 320 | 10% | 3461040 | All Buildings | CSA
| 3 30 81 | • Mat Foundation — Concrete | 0 | LS | 1824000 | 10% | 0 | All Buildings | CSA
| 3 30 82 | • Mat Foundation — Rebar | 0 | LS | 760000 | 10% | 0 | All Buildings | CSA
| 3 30 83 | • Mat Foundation — Forming & Finishing | 0 | LS | 456000 | 10% | 0 | All Buildings | CSA
15 | 03 30 95 | Cast-in-Place — Pile Caps & Grade Beams | 4200 | CY | 380 | 10% | 1817046 | All Buildings | CSA
16 | 03 35 50 | Concrete Floor Hardener & Sealer | 600000 | SF | 1.4 | 10% | 956340 | All Buildings | CSA
17 | 03 15 50 | Waterstops & Construction Joints | 9000 | LF | 18 | 10% | 184437 | All Buildings | CSA
18 | 03 62 50 | Non-Shrink Grout — Equipment Base Plates | 1800 | CF | 45 | 10% | 92218.5 | All Buildings | CSA
19 | 03 11 50 | Concrete Formwork — Walls & Columns | 90000 | SF | 9 | 10% | 922185 | All Buildings | CSA
|  | Subtotal — CONCRETE |  |  |  |  | 33466040.3876
DIVISION 04 — MASONRY | [8 empty] | CSA
1 | 04 05 00 | Masonry Common Work — Mortar, Grout & Reinforcing | 1 | LS | 180000 | 10% | 204930 | All Buildings | CSA
2 | 04 20 00 | CMU — Fire-Rated Walls (Electrical / UPS / Battery Rooms) — breakdown ↓ | 96000 | SF | 22 | 10% | 2404512 | All Buildings | CSA
| 4 20 01 | • CMU Walls — Block & Mortar | 0 | LS | 1267200 | 10% | 0 | All Buildings | CSA
| 4 20 02 | • CMU Walls — Reinforcing & Grout | 0 | LS | 528000 | 10% | 0 | All Buildings | CSA
| 4 20 03 | • CMU Walls — Install | 0 | LS | 316800 | 10% | 0 | All Buildings | CSA
3 | 04 20 10 | CMU — Generator Yard Screen Walls | 9000 | SF | 26 | 10% | 266409 | Shared | CSA
4 | 04 22 00 | Reinforced Masonry — Security / Blast-Resistant Walls | 14000 | SF | 40 | 10% | 637560 | All Buildings | CSA
5 | 04 23 00 | Architectural Masonry Veneer — Office / Entry | 12000 | SF | 30 | 10% | 409860 | All Buildings | CSA
6 | 04 01 00 | Masonry Cleaning, Sealing & Restoration | 1 | LS | 70000 | 10% | 79695 | All Buildings | CSA
7 | 04 73 00 | Manufactured Stone Veneer — Entry | 18000 | SF | 38 | 10% | 778734 | All Buildings | CSA
8 | 04 21 50 | Brick Veneer — Office Facade | 24000 | SF | 32 | 10% | 874368 | All Buildings | CSA
|  | Subtotal — MASONRY |  |  |  |  | 5656068
DIVISION 05 — METALS / STRUCTURAL STEEL | [8 empty] | CSA
1 | 05 12 00 | Structural Steel Framing — Building — breakdown ↓ | 3200 | TON | 3500 | 10% | 12751200 | All Buildings | CSA
| 5 12 01 | • Steel — Fabricated (Columns/Beams) | 0 | LS | 6720000 | 10% | 0 | All Buildings | CSA
| 5 12 02 | • Steel — Erection & Connections | 0 | LS | 2800000 | 10% | 0 | All Buildings | CSA
| 5 12 03 | • Steel — Shop Priming & Coatings | 0 | LS | 896000 | 10% | 0 | All Buildings | CSA
| 5 12 04 | • Steel — Detailing & Engineering | 0 | LS | 784000 | 10% | 0 | All Buildings | CSA
2 | 05 12 10 | Structural Steel — Mezzanine / Elevated Platforms | 160 | TON | 3850 | 10% | 701316 | All Buildings | CSA
3 | 05 12 20 | Structural Steel — Generator / Equipment Support — breakdown ↓ | 562.5 | TON | 3850 | 10% | 2465564.0625 | All Buildings | CSA
| 5 12 21 | • Gen Steel — Fabricated | 0 | LS | 1299375 | 10% | 0 | All Buildings | CSA
| 5 12 22 | • Gen Steel — Erection | 0 | LS | 606375 | 10% | 0 | All Buildings | CSA
| 5 12 23 | • Gen Steel — Coatings | 0 | LS | 259875 | 10% | 0 | All Buildings | CSA
4 | 05 21 00 | Steel Joists — breakdown ↓ | 560000 | SF | 4.2 | 10% | 2677752 | All Buildings | CSA
| 5 21 01 | • Steel Joists — Joists | 0 | LS | 1528800 | 10% | 0 | All Buildings | CSA
| 5 21 02 | • Steel Joists — Erection | 0 | LS | 588000 | 10% | 0 | All Buildings | CSA
| 5 21 03 | • Steel Joists — Accessories | 0 | LS | 235200 | 10% | 0 | All Buildings | CSA
5 | 05 31 00 | Steel Decking — Roof — breakdown ↓ | 484438.6277 | SF | 4.5 | 10% | 2481900.1995 | All Buildings | CSA
| 5 31 01 | • Roof Deck — Decking | 0 | LS | 1525981.6773 | 10% | 0 | All Buildings | CSA
| 5 31 02 | • Roof Deck — Fasteners & Accessories | 0 | LS | 326996.0737 | 10% | 0 | All Buildings | CSA
| 5 31 03 | • Roof Deck — Install | 0 | LS | 326996.0737 | 10% | 0 | All Buildings | CSA
6 | 05 31 10 | Steel Decking — Elevated Floors | 240000 | SF | 6 | 10% | 1639440 | All Buildings | CSA
7 | 05 40 00 | Cold-Formed Metal Framing — breakdown ↓ | 320000 | SF | 8.4 | 10% | 3060288 | All Buildings | CSA
| 5 40 01 | • CFMF — Studs & Track | 0 | LS | 1612800 | 10% | 0 | All Buildings | CSA
| 5 40 02 | • CFMF — Install | 0 | LS | 672000 | 10% | 0 | All Buildings | CSA
| 5 40 03 | • CFMF — Sheathing Attachment | 0 | LS | 403200 | 10% | 0 | All Buildings | CSA
8 | 05 50 00 | Metal Fabrications — Stairs, Railings, Ladders | 800000 | SF | 1.4 | 10% | 1275120 | All Buildings | CSA
9 | 05 51 00 | Metal Stairs — Interior | 20 | EA | 52500 | 10% | 1195425 | All Buildings | CSA
10 | 05 52 00 | Pipe / Equipment Supports — Seismic Bracing — breakdown ↓ | 1125 | EA | 5600 | 10% | 7172550 | All Buildings | CSA
| 5 52 01 | • Seismic Supports — Steel & Bracing | 0 | LS | 3780000 | 10% | 0 | All Buildings | CSA
| 5 52 02 | • Seismic Supports — Snubbers & Isolators | 0 | LS | 1575000 | 10% | 0 | All Buildings | CSA
| 5 52 03 | • Seismic Supports — Anchorage & Install | 0 | LS | 945000 | 10% | 0 | All Buildings | CSA
11 | 05 53 00 | Cable Tray / Ladder Rack Support Steel | 90000 | LF | 17.5 | 10% | 1793137.5 | All Buildings | CSA
12 | 05 12 50 | Anchor Bolts & Embed Plates — Structural | 1 | LS | 220000 | 10% | 250470 | All Buildings | CSA
13 | 05 31 50 | Equipment / Roof Screen Framing | 180000 | LB | 4.5 | 10% | 922185 | All Buildings | CSA
14 | 05 51 50 | Catwalks & Crossover Platforms | 12000 | SF | 95 | 10% | 1297890 | All Buildings | CSA
15 | 05 50 60 | Loose Lintels & Misc Embedded Steel | 120000 | LB | 4 | 10% | 546480 | All Buildings | CSA
16 | 05 53 50 | Metal Bar Grating — Trenches / Pits | 14000 | SF | 38 | 10% | 605682 | All Buildings | CSA
|  | Subtotal — METALS / STRUCTURAL STEEL |  |  |  |  | 40836399.762
DIVISION 06 — WOOD, PLASTICS & COMPOSITES | [8 empty] | CSA
1 | 06 10 00 | Rough Carpentry — Blocking, Nailers & Curbs | 40000 | SF | 2.5 | 10% | 113850 | All Buildings | CSA
2 | 06 16 00 | Sheathing — Roof / Wall | 64000 | SF | 3 | 10% | 218592 | All Buildings | CSA
3 | 06 64 00 | FRP Wall Liner Panels — Wet / Service Areas | 18000 | SF | 6 | 10% | 122958 | All Buildings | CSA
4 | 06 83 00 | Fiberglass Grating — Equipment Platforms / Trenches | 6000 | SF | 22 | 10% | 150282 | All Buildings | CSA
5 | 06 10 10 | Plywood Backboards — Telecom / Electrical | 120 | EA | 180 | 10% | 24591.6 | All Buildings | CSA
6 | 06 41 00 | Architectural Millwork — Lobby / Reception | 1 | LS | 350000 | 10% | 398475 | All Buildings | CSA
7 | 6 64 01 | Solid Surface Fabrications — Reception / Break | 1 | LS | 180000 | 10% | 204930 | All Buildings | CSA
|  | Subtotal — WOOD, PLASTICS & COMPOSITES |  |  |  |  | 1233678.6
DIVISION 07 — THERMAL & MOISTURE PROTECTION | [8 empty] | CSA
1 | 07 11 00 | Dampproofing — Foundation | 40000 | SF | 2.8 | 10% | 127512 | All Buildings | CSA
2 | 07 13 00 | Sheet Membrane Waterproofing | 80000 | SF | 8.4 | 10% | 765072 | All Buildings | CSA
3 | 07 21 00 | Building Insulation — Walls — breakdown ↓ | 480000 | SF | 4.2 | 10% | 2295216 | All Buildings | CSA
| 7 21 01 | • Wall Insulation — Insulation | 0 | LS | 1310400 | 10% | 0 | All Buildings | CSA
| 7 21 02 | • Wall Insulation — Vapor Barrier | 0 | LS | 403200 | 10% | 0 | All Buildings | CSA
| 7 21 03 | • Wall Insulation — Install | 0 | LS | 302400 | 10% | 0 | All Buildings | CSA
4 | 07 22 00 | Roof Insulation — breakdown ↓ | 800000 | SF | 2.8 | 10% | 2550240 | All Buildings | CSA
| 7 22 01 | • Roof Insulation — Board | 0 | LS | 1568000 | 10% | 0 | All Buildings | CSA
| 7 22 02 | • Roof Insulation — Fasteners & Adhesive | 0 | LS | 403200 | 10% | 0 | All Buildings | CSA
| 7 22 03 | • Roof Insulation — Install | 0 | LS | 268800 | 10% | 0 | All Buildings | CSA
5 | 07 41 00 | Metal Wall Panels — Insulated — breakdown ↓ | 480000 | SF | 18 | 10% | 9836640 | All Buildings | CSA
| 7 41 01 | • Wall Panels — Panels & Insulation | 0 | LS | 5616000 | 10% | 0 | All Buildings | CSA
| 7 41 02 | • Wall Panels — Subgirts & Attachment | 0 | LS | 1728000 | 10% | 0 | All Buildings | CSA
| 7 41 03 | • Wall Panels — Flashing & Trim | 0 | LS | 1296000 | 10% | 0 | All Buildings | CSA
6 | 07 42 00 | Metal Soffit Panels | 40000 | SF | 17.5 | 10% | 796950 | All Buildings | CSA
7 | 07 51 00 | Built-Up Roofing (BUR) / Modified Bitumen | 80000 | SF | 9.8 | 10% | 892584 | All Buildings | CSA
8 | 07 52 00 | Single-Ply Membrane Roofing (TPO/EPDM) — breakdown ↓ | 800000 | SF | 8 | 10% | 7286400 | All Buildings | CSA
| 7 52 01 | • TPO Roofing — Membrane & Insulation | 0 | LS | 3968000 | 10% | 0 | All Buildings | CSA
| 7 52 02 | • TPO Roofing — Fasteners & Adhesive | 0 | LS | 1152000 | 10% | 0 | All Buildings | CSA
| 7 52 03 | • TPO Roofing — Flashing & Details | 0 | LS | 1280000 | 10% | 0 | All Buildings | CSA
9 | 07 62 00 | Sheet Metal Flashing & Trim | 800000 | SF | 1.05 | 10% | 956340 | All Buildings | CSA
10 | 07 71 00 | Roof Specialties — Hatches, Vents, Curbs | 50 | EA | 2800 | 10% | 159390 | All Buildings | CSA
11 | 07 72 00 | Roof Accessories — Walkway Pads, Fall Protection | 800000 | SF | 0.35 | 10% | 318780 | All Buildings | CSA
12 | 07 81 00 | Applied Fireproofing — Spray — breakdown ↓ | 3200 | TON | 2450 | 10% | 8925840 | All Buildings | CSA
| 7 81 01 | • Fireproofing — Material & Application | 0 | LS | 5880000 | 10% | 0 | All Buildings | CSA
| 7 81 02 | • Fireproofing — Prep & Masking | 0 | LS | 1176000 | 10% | 0 | All Buildings | CSA
| 7 81 03 | • Fireproofing — Patching & Touch-Up | 0 | LS | 784000 | 10% | 0 | All Buildings | CSA
13 | 07 84 00 | Firestopping / Penetration Sealing | 11250 | EA | 35 | 10% | 448284.375 | All Buildings | CSA
14 | 07 92 00 | Joint Sealants | 800000 | SF | 0.35 | 10% | 318780 | All Buildings | CSA
15 | 07 27 00 | Air & Vapor Barrier — Building Envelope | 280000 | SF | 2.2 | 10% | 701316 | All Buildings | CSA
16 | 07 95 00 | Expansion Joint Cover Assemblies | 4200 | LF | 65 | 10% | 310810.5 | All Buildings | CSA
17 | 07 18 00 | Traffic Coating — Ramps / Parking Deck | 40000 | SF | 7 | 10% | 318780 | All Buildings | CSA
18 | 07 72 50 | Roof Walkway / Equipment Ballast Pavers | 36000 | SF | 12 | 10% | 491832 | All Buildings | CSA
19 | 7 71 01 | Gutters, Downspouts & Scuppers | 8000 | LF | 28 | 10% | 255024 | All Buildings | CSA
20 | 07 13 50 | Below-Grade Waterproofing — Pits / Vaults | 40000 | SF | 9 | 10% | 409860 | All Buildings | CSA
|  | Subtotal — THERMAL & MOISTURE PROTECTION |  |  |  |  | 38165650.875
DIVISION 08 — OPENINGS | [8 empty] | CSA
1 | 08 11 00 | Hollow Metal Doors & Frames — Interior | 320 | EA | 1200 | 10% | 437184 | All Buildings | CSA
2 | 08 11 10 | Hollow Metal Doors & Frames — Exterior | 50 | EA | 2450 | 10% | 139466.25 | All Buildings | CSA
3 | 08 14 00 | Acoustical Doors — Generator / Mech Rooms | 20 | EA | 5950 | 10% | 135481.5 | All Buildings | CSA
4 | 08 31 00 | Access Doors & Panels | 266.6667 | EA | 560 | 10% | 170016 | All Buildings | CSA
5 | 08 33 00 | Overhead Coiling Doors — Loading Dock | 8 | EA | 8000 | 10% | 72864 | All Buildings | CSA
6 | 08 34 00 | High-Speed Roll-Up Doors | 4 | EA | 17500 | 10% | 79695 | All Buildings | CSA
7 | 08 36 00 | Sectional Overhead Doors | 8 | EA | 8400 | 10% | 76507.2 | All Buildings | CSA
8 | 08 41 00 | Aluminum Entrances — Storefront | 16000 | SF | 59.5 | 10% | 1083852 | All Buildings | CSA
9 | 08 44 00 | Curtain Wall System — breakdown ↓ | 24221.9314 | SF | 87.5 | 10% | 2412958.5274 | All Buildings | CSA
| 8 44 01 | • Curtain Wall — Framing & Glazing | 0 | LS | 1377622.3476 | 10% | 0 | All Buildings | CSA
| 8 44 02 | • Curtain Wall — Install | 0 | LS | 423883.7993 | 10% | 0 | All Buildings | CSA
| 8 44 03 | • Curtain Wall — Sealants & Flashing | 0 | LS | 317912.8495 | 10% | 0 | All Buildings | CSA
10 | 08 51 00 | Aluminum Windows | 24000 | SF | 45.5 | 10% | 1243242 | All Buildings | CSA
11 | 08 71 00 | Door Hardware — Standard | 320 | EA | 1050 | 10% | 382536 | All Buildings | CSA
12 | 08 71 10 | Door Hardware — Electrified (Access Control) | 400 | EA | 2450 | 10% | 1115730 | All Buildings | CSA
13 | 08 80 00 | Glazing | 64000 | SF | 24.5 | 10% | 1785168 | All Buildings | CSA
14 | 08 81 00 | Security Glazing — Blast Rated | 8000 | SF | 122.5 | 10% | 1115730 | All Buildings | CSA
15 | 08 90 00 | Louvers & Mechanical Vents | 24000 | SF | 38 | 10% | 1038312 | All Buildings | CSA
16 | 08 31 50 | Fire-Rated Door Assemblies — Rated Corridors | 240 | EA | 2400 | 10% | 655776 | All Buildings | CSA
17 | 08 62 00 | Skylights / Glazed Smoke Vents | 36 | EA | 6500 | 10% | 266409 | All Buildings | CSA
18 | 08 71 60 | Automatic Door Operators — ADA / Vestibule | 48 | EA | 6500 | 10% | 355212 | All Buildings | CSA
19 | 8 14 01 | Wood Doors — Office / Administrative | 320 | EA | 850 | 10% | 309672 | All Buildings | CSA
20 | 8 36 01 | Sectional Overhead Doors — Loading / Service | 36 | EA | 6500 | 10% | 266409 | All Buildings | CSA
21 | 8 71 01 | Door Hardware Sets — Finish Hardware | 620 | EA | 850 | 10% | 599989.5 | All Buildings | CSA
|  | Subtotal — OPENINGS |  |  |  |  | 13742209.9774
DIVISION 09 — FINISHES | [8 empty] | CSA
1 | 09 21 00 | Gypsum Board — Interior Partitions — breakdown ↓ | 960000 | SF | 6 | 10% | 6557760 | All Buildings | CSA
| 9 21 01 | • Gypsum — Framing & Studs | 0 | LS | 2304000 | 10% | 0 | All Buildings | CSA
| 9 21 02 | • Gypsum — Board & Install | 0 | LS | 2304000 | 10% | 0 | All Buildings | CSA
| 9 21 03 | • Gypsum — Taping & Finishing | 0 | LS | 1152000 | 10% | 0 | All Buildings | CSA
2 | 09 22 00 | Metal Stud Framing — Interior | 480000 | SF | 2.8 | 10% | 1530144 | All Buildings | CSA
3 | 09 51 00 | Acoustical Ceilings — Office / Support | 120000 | SF | 4.2 | 10% | 573804 | All Buildings | CSA
4 | 09 65 00 | Resilient Flooring — VCT / LVT | 80000 | SF | 3.5 | 10% | 318780 | All Buildings | CSA
5 | 09 68 00 | Carpet — Office Areas | 40000 | SF | 5.6 | 10% | 255024 | All Buildings | CSA
6 | 09 69 00 | Raised Access Floor — Data Halls — breakdown ↓ | 440000 | SF | 22 | 10% | 11020680 | All Buildings | CSA
| 9 69 01 | • Raised Floor — Panels & Pedestals | 0 | LS | 6776000 | 10% | 0 | All Buildings | CSA
| 9 69 02 | • Raised Floor — Ramps, Stairs & Transitions | 0 | LS | 1161600 | 10% | 0 | All Buildings | CSA
| 9 69 03 | • Raised Floor — Cutouts, Grommets & Accessories | 0 | LS | 968000 | 10% | 0 | All Buildings | CSA
| 9 69 04 | • Raised Floor — Leveling & Install | 0 | LS | 774400 | 10% | 0 | All Buildings | CSA
7 | 09 69 10 | Raised Access Floor — Electrical Rooms | 40000 | SF | 28 | 10% | 1275120 | All Buildings | CSA
8 | 09 69 20 | Raised Floor Accessories — Grommets, Ramps, Cutouts | 440000 | SF | 1.4 | 10% | 701316 | All Buildings | CSA
9 | 09 72 00 | Wall Coverings — Epoxy Paint (Data Halls) | 660000 | SF | 2.8 | 10% | 2103948 | All Buildings | CSA
10 | 09 91 00 | Interior Painting — Standard | 480000 | SF | 1.4 | 10% | 765072 | All Buildings | CSA
11 | 09 96 00 | Epoxy Flooring — Battery / Generator Rooms | 80000 | SF | 6 | 10% | 546480 | All Buildings | CSA
12 | 09 97 00 | Anti-Static / ESD Flooring — Data Halls — breakdown ↓ | 440000 | SF | 5.6 | 10% | 2805264 | All Buildings | CSA
| 9 97 01 | • ESD Flooring — Material | 0 | LS | 1601600 | 10% | 0 | All Buildings | CSA
| 9 97 02 | • ESD Flooring — Install | 0 | LS | 616000 | 10% | 0 | All Buildings | CSA
| 9 97 03 | • ESD Flooring — Grounding | 0 | LS | 246400 | 10% | 0 | All Buildings | CSA
13 | 09 30 00 | Tiling — Restrooms / Wet Areas | 18000 | SF | 12 | 10% | 245916 | All Buildings | CSA
14 | 09 77 00 | Acoustic Wall Panels — NOC / Conference | 24000 | SF | 14 | 10% | 382536 | All Buildings | CSA
15 | 09 67 50 | Resinous Flooring — Mechanical / Pump Rooms | 80000 | SF | 9 | 10% | 819720 | All Buildings | CSA
16 | 09 22 50 | Gypsum Ceilings & Soffits — Hard-Lid | 60000 | SF | 9 | 10% | 614790 | All Buildings | CSA
17 | 09 65 50 | Resilient Base & Accessories | 38000 | LF | 6 | 10% | 259578 | All Buildings | CSA
18 | 9 68 01 | Carpet & Resilient Flooring — Office Areas | 120000 | SF | 6 | 10% | 819720 | All Buildings | CSA
19 | 09 91 50 | Intumescent Coatings — Exposed Structural Steel | 80000 | SF | 4 | 10% | 364320 | All Buildings | CSA
20 | 09 67 00 | Epoxy / Resinous Floor Coating — MEP & BOH | 120000 | SF | 9 | 10% | 1229580 | All Buildings | CSA
|  | Subtotal — FINISHES |  |  |  |  | 33189552
DIVISION 10 — SPECIALTIES | [8 empty] | CSA
1 | 10 14 00 | Signage — Interior Wayfinding | 160 | EA | 1050 | 10% | 191268 | All Buildings | CSA
2 | 10 14 10 | Signage — Exterior / Monument | 3 | EA | 17500 | 10% | 59771.25 | All Buildings | CSA
3 | 10 14 20 | Safety Signage — Arc Flash / Hazmat | 400 | EA | 175 | 10% | 79695 | All Buildings | CSA
4 | 10 21 00 | Toilet Partitions | 80 | EA | 3150 | 10% | 286902 | All Buildings | CSA
5 | 10 26 00 | Wall Protection — Corner Guards | 1600 | LF | 24.5 | 10% | 44629.2 | All Buildings | CSA
6 | 10 28 00 | Toilet & Bath Accessories | 160 | EA | 840 | 10% | 153014.4 | All Buildings | CSA
7 | 10 44 00 | Fire Extinguishers & Cabinets | 266.6667 | EA | 350 | 10% | 106260 | All Buildings | CSA
8 | 10 55 00 | Postal Specialties / Delivery Lockers | 1 | LS | 17500 | 10% | 19923.75 | All Buildings | CSA
9 | 10 73 00 | Protective Covers — Equipment Pads | 20 | EA | 3500 | 10% | 79695 | All Buildings | CSA
10 | 10 75 00 | Flagpoles | 3 | EA | 5950 | 10% | 20322.225 | All Buildings | CSA
11 | 10 21 50 | Lockers & Locker Room Benches | 120 | EA | 280 | 10% | 38253.6 | All Buildings | CSA
12 | 10 26 50 | Wall & Door Protection — Impact Rails | 18000 | LF | 28 | 10% | 573804 | All Buildings | CSA
13 | 10 73 01 | Exterior Canopies & Walkway Covers | 16000 | SF | 65 | 10% | 1184040 | All Buildings | CSA
14 | 10 11 50 | Visual Display Boards — Markerboards / Tackboards | 180 | EA | 480 | 10% | 98366.4 | All Buildings | CSA
15 | 10 22 50 | Operable / Demountable Partitions — Conference | 12000 | SF | 65 | 10% | 888030 | All Buildings | CSA
16 | 10 28 01 | Toilet & Bath Accessories | 280 | EA | 220 | 10% | 70131.6 | All Buildings | CSA
17 | 10 21 13 | Toilet Partitions — Phenolic | 120 | EA | 850 | 10% | 116127 | All Buildings | CSA
|  | Subtotal — SPECIALTIES |  |  |  |  | 4010233.425
DIVISION 11 — EQUIPMENT | [8 empty] | CSA
1 | 11 13 00 | Loading Dock Equipment — Levelers, Seals, Bumpers | 9 | EA | 14000 | 10% | 143451 | All Buildings | CSA
2 | 11 13 10 | Dock Lifts / Scissor Lifts — Equipment Handling | 6 | EA | 28000 | 10% | 191268 | All Buildings | CSA
3 | 11 30 00 | Residential / Pantry Appliances — Break Rooms | 1 | LS | 60000 | 10% | 68310 | All Buildings | CSA
4 | 11 40 00 | Foodservice Equipment — Staff Café | 1 | LS | 180000 | 10% | 204930 | All Buildings | CSA
5 | 11 24 00 | Facility Maintenance Equipment — Window Washing / Davits | 1 | LS | 120000 | 10% | 136620 | All Buildings | CSA
6 | 11 53 00 | Battery / Laboratory Test Equipment | 1 | LS | 90000 | 10% | 102465 | All Buildings | CSA
7 | 11 82 00 | Solid Waste Handling — Compactors & Balers | 3 | EA | 30000 | 10% | 102465 | Shared | CSA
8 | 11 13 50 | Loading Dock Shelters / Canopies | 8 | EA | 12000 | 10% | 109296 | All Buildings | CSA
9 | 11 12 00 | Parking Control Equipment — Gates / Ticketing | 1 | LS | 220000 | 10% | 250470 | All Buildings | CSA
10 | 11 13 60 | Vehicle Scale — Truck Weighing | 2 | EA | 95000 | 10% | 216315 | All Buildings | CSA
|  | Subtotal — EQUIPMENT |  |  |  |  | 1525590
DIVISION 12 — FURNISHINGS | [8 empty] | CSA
1 | 12 21 00 | Window Treatments — Blinds / Shades | 8000 | SF | 8 | 10% | 72864 | All Buildings | CSA
2 | 12 24 00 | Entrance Mats & Grilles | 2500 | SF | 18 | 10% | 51232.5 | All Buildings | CSA
3 | 12 35 00 | Specialty Casework — Break / Copy / Support | 600 | LF | 280 | 10% | 191268 | All Buildings | CSA
4 | 12 48 00 | Operations Console Systems — NOC / SOC | 48 | EA | 6500 | 10% | 355212 | All Buildings | CSA
5 | 12 52 00 | Institutional Furniture — Office / Conference | 1 | LS | 220000 | 10% | 250470 | All Buildings | CSA
6 | 12 93 00 | Site Furnishings — Benches, Bike Racks, Receptacles | 1 | LS | 40000 | 10% | 45540 | Shared | CSA
7 | 12 36 00 | Countertops — Break / Pantry / Casework | 1 | LS | 220000 | 10% | 250470 | All Buildings | CSA
|  | Subtotal — FURNISHINGS |  |  |  |  | 1217056.5
DIVISION 14 — CONVEYING EQUIPMENT | [8 empty] | CSA
1 | 14 21 00 | Passenger Elevators — Traction (Office Core) | 6 | EA | 140000 | 10% | 956340 | All Buildings | CSA
2 | 14 21 10 | Freight Elevators — Heavy Equipment (12,000 lb) | 6 | EA | 320000 | 10% | 2185920 | All Buildings | CSA
3 | 14 24 00 | Hydraulic Elevators — Service / Low-Rise | 3 | EA | 95000 | 10% | 324472.5 | All Buildings | CSA
4 | 14 42 00 | Material Lifts / Vertical Reciprocating Conveyors | 6 | EA | 45000 | 10% | 307395 | All Buildings | CSA
5 | 14 91 00 | Hoists & Monorail Cranes — Equipment Rigging | 3 | EA | 70000 | 10% | 239085 | All Buildings | CSA
6 | 14 92 00 | Facility Conveying — Tube / Material Transport | 1 | LS | 80000 | 10% | 91080 | Shared | CSA
|  | Subtotal — CONVEYING EQUIPMENT |  |  |  |  | 4104292.5
DIVISION 21 — FIRE SUPPRESSION | [8 empty] | MEP
1 | 21 05 00 | Fire Suppression — Common Work | 800000 | SF | 0.35 | 10% | 318780 | All Buildings | MEP
2 | 21 11 00 | Wet Sprinkler System — Office / Support Areas | 240000 | SF | 3.5 | 10% | 956340 | All Buildings | MEP
3 | 21 12 00 | Dry Sprinkler System — Loading Dock / Generator Area | 40000 | SF | 5.6 | 10% | 255024 | All Buildings | MEP
4 | 21 13 00 | Pre-Action Sprinkler System — Data Halls — breakdown ↓ | 440000 | SF | 6 | 10% | 3005640 | All Buildings | MEP
| 21 13 01 | • Pre-Action — Piping & Heads | 0 | LS | 1320000 | 10% | 0 | All Buildings | MEP
| 21 13 02 | • Pre-Action — Valves & Risers | 0 | LS | 792000 | 10% | 0 | All Buildings | MEP
| 21 13 03 | • Pre-Action — Controls | 0 | LS | 528000 | 10% | 0 | All Buildings | MEP
5 | 21 13 10 | Pre-Action Sprinkler — Electrical Rooms | 80000 | SF | 5 | 10% | 455400 | All Buildings | MEP
6 | 21 22 00 | Clean Agent System — FM-200 (Data Halls) — breakdown ↓ | 440000 | SF | 12 | 10% | 6011280 | All Buildings | MEP
| 21 22 01 | • FM-200 — Agent & Cylinders | 0 | LS | 2640000 | 10% | 0 | All Buildings | MEP
| 21 22 02 | • FM-200 — Piping & Nozzles | 0 | LS | 1320000 | 10% | 0 | All Buildings | MEP
| 21 22 03 | • FM-200 — Detection & Controls | 0 | LS | 792000 | 10% | 0 | All Buildings | MEP
| 21 22 04 | • FM-200 — Install | 0 | LS | 528000 | 10% | 0 | All Buildings | MEP
7 | 21 22 10 | Clean Agent System — Novec 1230 (Alternate) | 0 | LS | 0 | 10% | 0 | All Buildings | MEP
8 | 21 22 20 | Clean Agent — UPS / Battery Rooms | 64000 | SF | 22 | 10% | 1603008 | All Buildings | MEP
9 | 21 30 00 | VESDA — Very Early Smoke Detection Apparatus | 440000 | SF | 3 | 10% | 1502820 | All Buildings | MEP
10 | 21 30 10 | Smoke Detection — Duct / Plenum Detectors | 800000 | SF | 0.6 | 10% | 546480 | All Buildings | MEP
11 | 21 31 00 | Fire Alarm / Mass Notification System — breakdown ↓ | 800000 | SF | 4 | 10% | 3643200 | All Buildings | MEP
| 21 31 01 | • Fire Alarm — Panels & Devices | 0 | LS | 1760000 | 10% | 0 | All Buildings | MEP
| 21 31 02 | • Fire Alarm — Wiring | 0 | LS | 800000 | 10% | 0 | All Buildings | MEP
| 21 31 03 | • Fire Alarm — Programming & Test | 0 | LS | 640000 | 10% | 0 | All Buildings | MEP
12 | 21 32 00 | Fire Alarm Control Panels (FACP) | 9 | EA | 24500 | 10% | 251039.25 | All Buildings | MEP
13 | 21 33 00 | Smoke Evacuation / Purge System | 80000 | SF | 5.6 | 10% | 510048 | All Buildings | MEP
14 | 21 34 00 | Standpipe System | 3 | EA | 52500 | 10% | 179313.75 | All Buildings | MEP
15 | 21 35 00 | Fire Pump | 3 | EA | 60000 | 10% | 204930 | All Buildings | MEP
16 | 21 40 00 | Fire Protection Water Storage Tank | 3 | EA | 175000 | 10% | 597712.5 | All Buildings | MEP
17 | 21 16 00 | Foam Suppression — Fuel Storage / Generator | 1 | LS | 650000 | 10% | 740025 | All Buildings | MEP
18 | 21 11 50 | Fire Water Yard Loop & Hydrants | 7200 | LF | 110 | 10% | 901692 | All Buildings | MEP
19 | 21 12 50 | Jockey Pump & Fire Pump Test Header | 1 | LS | 180000 | 10% | 204930 | All Buildings | MEP
20 | 21 11 60 | Fire Department Connections & Hydrant Valves | 36 | EA | 3500 | 10% | 143451 | All Buildings | MEP
21 | 21 13 70 | Sprinkler Piping, Heads & Risers — Office/Support | 120000 | SF | 4 | 10% | 546480 | All Buildings | MEP
|  | Subtotal — FIRE SUPPRESSION |  |  |  |  | 22577593.5
DIVISION 22 — PLUMBING | [8 empty] | MEP
1 | 22 10 00 | Domestic Water — Plumbing Fixtures & Trim | 400 | FIX | 2500 | 10% | 1138500 | All Buildings | MEP
2 | 22 11 00 | Domestic Hot Water System | 266.6667 | FIX | 3850 | 10% | 1168860 | All Buildings | MEP
3 | 22 13 00 | Sanitary Waste & Vent Piping | 320 | FIX | 2800 | 10% | 1020096 | All Buildings | MEP
4 | 22 14 00 | Storm Drainage — Interior Piping | 800000 | SF | 0.84 | 10% | 765072 | All Buildings | MEP
5 | 22 15 00 | Make-Up Water — Cooling Towers / Humidification — breakdown ↓ | 12825 | GPM | 800 | 10% | 11681010 | All Buildings | MEP
| 22 15 01 | • Makeup Water — Storage Tanks | 0 | LS | 4104000 | 10% | 0 | All Buildings | MEP
| 22 15 02 | • Makeup Water — Treatment & Filtration | 0 | LS | 3078000 | 10% | 0 | All Buildings | MEP
| 22 15 03 | • Makeup Water — Pumps & Piping | 0 | LS | 2052000 | 10% | 0 | All Buildings | MEP
| 22 15 04 | • Makeup Water — Controls | 0 | LS | 1026000 | 10% | 0 | All Buildings | MEP
6 | 22 16 00 | Condensate Drain — CRAH / AHU Units | 1282.5 | GPM | 140 | 10% | 204417.675 | All Buildings | MEP
7 | 22 17 00 | Emergency Shower & Eyewash Stations | 80 | EA | 3150 | 10% | 286902 | All Buildings | MEP
8 | 22 30 00 | Acid Neutralization Tank — Battery Room | 3 | EA | 15000 | 10% | 51232.5 | All Buildings | MEP
9 | 22 40 00 | Grease Interceptor — Kitchen / Café | 1 | EA | 17500 | 10% | 19923.75 | All Buildings | MEP
10 | 22 50 00 | Natural Gas Piping — Generator Support | 22500 | LF | 45.5 | 10% | 1165539.375 | All Buildings | MEP
11 | 22 60 00 | Compressed Air System — Generator Starting | 5625 | LF | 59.5 | 10% | 381041.7188 | All Buildings | MEP
12 | 22 70 00 | Backflow Prevention Assemblies | 10 | EA | 8400 | 10% | 95634 | All Buildings | MEP
13 | 22 14 50 | Storm / Sump Pump Systems | 24 | EA | 9500 | 10% | 259578 | All Buildings | MEP
14 | 22 31 50 | Reverse Osmosis / DI Water System | 1 | LS | 1200000 | 10% | 1366200 | All Buildings | MEP
15 | 22 14 60 | Trench Drains — Mechanical / Generator Rooms | 4800 | LF | 95 | 10% | 519156 | All Buildings | MEP
16 | 22 67 00 | Process Water Piping — Liquid Cooling Makeup | 9000 | LF | 110 | 10% | 1127115 | All Buildings | MEP
17 | 22 13 60 | Floor Drains, Roof Drains & Cleanouts | 480 | EA | 650 | 10% | 355212 | All Buildings | MEP
18 | 22 07 50 | Plumbing Piping Insulation | 22000 | LF | 9 | 10% | 225423 | All Buildings | MEP
19 | 22 33 50 | Domestic Water Heaters & Recirculation | 24 | EA | 12000 | 10% | 327888 | All Buildings | MEP
20 | 22 11 50 | Hose Bibbs & Wall Hydrants | 120 | EA | 450 | 10% | 61479 | All Buildings | MEP
21 | 22 66 00 | Emergency Eyewash & Safety Showers — Battery Rooms | 18 | EA | 4500 | 10% | 92218.5 | All Buildings | MEP
|  | Subtotal — PLUMBING |  |  |  |  | 22312498.5188
DIVISION 23 — HVAC / COOLING SYSTEMS | [8 empty] | MEP
1 | 23 05 00 | Mechanical Common Work — Hangers, Supports, Seismic — breakdown ↓ | 800000 | SF | 2.8 | 10% | 2550240 | All Buildings | MEP
| 23 05 01 | • Mech Common — Hangers & Supports | 0 | LS | 1232000 | 10% | 0 | All Buildings | MEP
| 23 05 02 | • Mech Common — Sleeves & Seals | 0 | LS | 560000 | 10% | 0 | All Buildings | MEP
| 23 05 03 | • Mech Common — Misc | 0 | LS | 448000 | 10% | 0 | All Buildings | MEP
2 | 23 05 10 | Mechanical Insulation | 800000 | SF | 2.1 | 10% | 1912680 | All Buildings | MEP
3 | 23 07 00 | HVAC Ductwork Insulation | 240000 | SF | 3.5 | 10% | 956340 | All Buildings | MEP
4 | 23 09 00 | Building Management System (BMS) — Controls — breakdown ↓ | 9000 | PT | 350 | 10% | 3586275 | All Buildings | MEP
| 23 09 01 | • BMS — Controllers & Devices | 0 | LS | 1575000 | 10% | 0 | All Buildings | MEP
| 23 09 02 | • BMS — Software & Graphics | 0 | LS | 787500 | 10% | 0 | All Buildings | MEP
| 23 09 03 | • BMS — Integration | 0 | LS | 787500 | 10% | 0 | All Buildings | MEP
5 | 23 09 10 | DCIM Integration — Environmental Monitoring — breakdown ↓ | 4500 | PT | 525 | 10% | 2689706.25 | All Buildings | MEP
| 23 09 11 | • DCIM — Software & Sensors | 0 | LS | 1299375 | 10% | 0 | All Buildings | MEP
| 23 09 12 | • DCIM — Integration | 0 | LS | 590625 | 10% | 0 | All Buildings | MEP
| 23 09 13 | • DCIM — Install | 0 | LS | 472500 | 10% | 0 | All Buildings | MEP
6 | 23 21 00 | Centrifugal Chillers — Water-Cooled — breakdown ↓ | 25650 | TON | 800 | 10% | 23362020 | All Buildings | MEP
| 23 21 01 | • Chillers — Units | 0 | LS | 12722400 | 10% | 0 | All Buildings | MEP
| 23 21 02 | • Chillers — Refrigerant Charge & VFDs | 0 | LS | 2462400 | 10% | 0 | All Buildings | MEP
| 23 21 03 | • Chillers — Rigging & Install | 0 | LS | 3283200 | 10% | 0 | All Buildings | MEP
| 23 21 04 | • Chillers — Startup & Commissioning | 0 | LS | 2052000 | 10% | 0 | All Buildings | MEP
7 | 23 21 10 | Chiller Plant Pumps — Primary / Secondary | 7.2 | EA | 105000 | 10% | 860706 | All Buildings | MEP
8 | 23 21 20 | Chilled Water Piping — Primary Loop | 10800 | LF | 80 | 10% | 983664 | All Buildings | MEP
9 | 23 21 30 | Chilled Water Piping — Secondary / Tertiary — breakdown ↓ | 27000 | LF | 84 | 10% | 2582118 | All Buildings | MEP
| 23 21 31 | • CHW Piping (Sec) — Pipe & Fittings | 0 | LS | 1360800 | 10% | 0 | All Buildings | MEP
| 23 21 32 | • CHW Piping (Sec) — Valves & Specialties | 0 | LS | 567000 | 10% | 0 | All Buildings | MEP
| 23 21 33 | • CHW Piping (Sec) — Hangers & Install | 0 | LS | 340200 | 10% | 0 | All Buildings | MEP
10 | 23 22 00 | Cooling Towers — Induced Draft — breakdown ↓ | 25650 | TON | 200 | 10% | 5840505 | All Buildings | MEP
| 23 22 01 | • Cooling Towers — Towers | 0 | LS | 3180600 | 10% | 0 | All Buildings | MEP
| 23 22 02 | • Cooling Towers — Basins & Fans | 0 | LS | 923400 | 10% | 0 | All Buildings | MEP
| 23 22 03 | • Cooling Towers — Install & Rigging | 0 | LS | 615600 | 10% | 0 | All Buildings | MEP
| 23 22 04 | • Cooling Towers — Controls | 0 | LS | 410400 | 10% | 0 | All Buildings | MEP
11 | 23 22 10 | Condenser Water Piping | 8100 | LF | 91 | 10% | 839188.35 | All Buildings | MEP
12 | 23 22 20 | Condenser Water Treatment System | 15390 | TON | 35 | 10% | 613253.025 | All Buildings | MEP
13 | 23 23 00 | Computer Room Air Handlers (CRAH) — breakdown ↓ | 10260 | TON | 600 | 10% | 7008606 | All Buildings | MEP
| 23 23 01 | • CRAH — Units | 0 | LS | 3816720 | 10% | 0 | All Buildings | MEP
| 23 23 02 | • CRAH — Piping & Coils | 0 | LS | 1108080 | 10% | 0 | All Buildings | MEP
| 23 23 03 | • CRAH — Controls | 0 | LS | 738720 | 10% | 0 | All Buildings | MEP
| 23 23 04 | • CRAH — Install | 0 | LS | 492480 | 10% | 0 | All Buildings | MEP
14 | 23 23 10 | In-Row Cooling Units — breakdown ↓ | 880 | EA | 52500 | 10% | 52598700 | All Buildings | MEP
| 23 23 11 | • In-Row Cooling — Units (Equipment) | 0 | LS | 63525000 | 10% | 0 | All Buildings | MEP
| 23 23 12 | • In-Row Cooling — Refrigerant / CW Piping | 0 | LS | 20790000 | 10% | 0 | All Buildings | MEP
| 23 23 13 | • In-Row Cooling — Controls & Integration | 0 | LS | 13860000 | 10% | 0 | All Buildings | MEP
| 23 23 14 | • In-Row Cooling — Rigging, Install & Seismic | 0 | LS | 11550000 | 10% | 0 | All Buildings | MEP
| 23 23 15 | • In-Row Cooling — Startup & Commissioning | 0 | LS | 5775000 | 10% | 0 | All Buildings | MEP
15 | 23 23 20 | Rear Door Heat Exchangers (RDHx) | 880 | EA | 24500 | 10% | 24546060 | All Buildings | MEP
16 | 23 24 00 | Hot Aisle Containment System — breakdown ↓ | 5550.8593 | CAB | 800 | 10% | 5055722.6286 | All Buildings | MEP
| 23 24 01 | • Hot Aisle — Panels & Doors | 0 | LS | 2664412.4526 | 10% | 0 | All Buildings | MEP
| 23 24 02 | • Hot Aisle — Roof / Ceiling | 0 | LS | 1110171.8552 | 10% | 0 | All Buildings | MEP
| 23 24 03 | • Hot Aisle — Install | 0 | LS | 666103.1131 | 10% | 0 | All Buildings | MEP
17 | 23 24 10 | Cold Aisle Containment System | 0 | LS | 0 | 10% | 0 | All Buildings | MEP
18 | 23 25 00 | Economizer System — Waterside — breakdown ↓ | 25650 | TON | 100 | 10% | 2920252.5 | All Buildings | MEP
| 23 25 01 | • Economizer — Heat Exchangers | 0 | LS | 1410750 | 10% | 0 | All Buildings | MEP
| 23 25 02 | • Economizer — Piping & Valves | 0 | LS | 641250 | 10% | 0 | All Buildings | MEP
| 23 25 03 | • Economizer — Controls | 0 | LS | 513000 | 10% | 0 | All Buildings | MEP
19 | 23 25 10 | Economizer System — Airside | 3078 | TON | 175 | 10% | 613253.025 | All Buildings | MEP
20 | 23 30 00 | HVAC Air Handling Units — Office / Support | 80000 | SF | 12.6 | 10% | 1147608 | All Buildings | MEP
21 | 23 31 00 | HVAC Ductwork — Office / Support | 240000 | SF | 5.6 | 10% | 1530144 | All Buildings | MEP
22 | 23 34 00 | HVAC Fans — Exhaust / Ventilation | 20 | EA | 24500 | 10% | 557865 | All Buildings | MEP
23 | 23 36 00 | Humidification System — breakdown ↓ | 440000 | SF | 5.6 | 10% | 2805264 | All Buildings | MEP
| 23 36 01 | • Humidification — Units | 0 | LS | 1478400 | 10% | 0 | All Buildings | MEP
| 23 36 02 | • Humidification — Distribution & Piping | 0 | LS | 616000 | 10% | 0 | All Buildings | MEP
| 23 36 03 | • Humidification — Controls | 0 | LS | 369600 | 10% | 0 | All Buildings | MEP
24 | 23 37 00 | Air Filtration — Data Hall | 440000 | SF | 3.5 | 10% | 1753290 | All Buildings | MEP
25 | 23 38 00 | Refrigerant Piping — DX Systems | 9000 | LF | 56 | 10% | 573804 | All Buildings | MEP
26 | 23 40 00 | Make-Up Water System — breakdown ↓ | 7695 | GPM | 420 | 10% | 3679518.15 | All Buildings | MEP
| 23 40 01 | • Makeup Water Sys — Tanks | 0 | LS | 1292760 | 10% | 0 | All Buildings | MEP
| 23 40 02 | • Makeup Water Sys — Treatment | 0 | LS | 969570 | 10% | 0 | All Buildings | MEP
| 23 40 03 | • Makeup Water Sys — Pumps | 0 | LS | 646380 | 10% | 0 | All Buildings | MEP
| 23 40 04 | • Makeup Water Sys — Controls | 0 | LS | 323190 | 10% | 0 | All Buildings | MEP
27 | 23 50 00 | Testing, Adjusting & Balancing (TAB) — breakdown ↓ | 90 | MW | 24500 | 10% | 2510392.5 | All Buildings | MEP
| 23 50 01 | • TAB — Air Balancing | 0 | LS | 992250 | 10% | 0 | All Buildings | MEP
| 23 50 02 | • TAB — Water Balancing | 0 | LS | 771750 | 10% | 0 | All Buildings | MEP
| 23 50 03 | • TAB — Reporting | 0 | LS | 441000 | 10% | 0 | All Buildings | MEP
28 | 23 60 00 | Direct Liquid Cooling Infrastructure | 90000 | kW | 150 | 10% | 15369750 | All Buildings | MEP
29 | 23 65 00 | CDU — Coolant Distribution Units | 45 | EA | 175000 | 10% | 8965687.5 | All Buildings | MEP
30 | 23 70 00 | Thermal Energy Storage — breakdown ↓ | 45000 | kWh | 560 | 10% | 28690200 | All Buildings | MEP
| 23 70 01 | • TES — Storage Tanks | 0 | LS | 12600000 | 10% | 0 | All Buildings | MEP
| 23 70 02 | • TES — Glycol Charge & Water Treatment | 0 | LS | 3780000 | 10% | 0 | All Buildings | MEP
| 23 70 03 | • TES — Pumps & Piping | 0 | LS | 5040000 | 10% | 0 | All Buildings | MEP
| 23 70 04 | • TES — Controls & Insulation | 0 | LS | 2520000 | 10% | 0 | All Buildings | MEP
| 23 70 05 | • TES — Commissioning | 0 | LS | 1260000 | 10% | 0 | All Buildings | MEP
31 | 23 09 50 | Variable Frequency Drives — Mechanical — breakdown ↓ | 181.6645 | EA | 18000 | 10% | 3722850.2992 | All Buildings | MEP
| 23 09 51 | • VFDs — Drives | 0 | LS | 2288972.516 | 10% | 0 | All Buildings | MEP
| 23 09 52 | • VFDs — Enclosures | 0 | LS | 490494.1105 | 10% | 0 | All Buildings | MEP
| 23 09 53 | • VFDs — Install & Programming | 0 | LS | 490494.1105 | 10% | 0 | All Buildings | MEP
32 | 23 34 50 | Generator Room / Equipment Ventilation Fans — breakdown ↓ | 90 | EA | 22000 | 10% | 2254230 | All Buildings | MEP
| 23 34 51 | • Gen Vent — Fans | 0 | LS | 1089000 | 10% | 0 | All Buildings | MEP
| 23 34 52 | • Gen Vent — Ductwork & Louvers | 0 | LS | 594000 | 10% | 0 | All Buildings | MEP
| 23 34 53 | • Gen Vent — Controls | 0 | LS | 297000 | 10% | 0 | All Buildings | MEP
33 | 23 25 50 | Glycol Feed & Chemical Treatment | 1 | LS | 480000 | 10% | 546480 | All Buildings | MEP
34 | 23 33 00 | Air Terminal Units — VAV / Fan-Powered Boxes | 240 | EA | 1800 | 10% | 491832 | All Buildings | MEP
35 | 23 37 50 | Diffusers, Registers & Grilles | 2400 | EA | 220 | 10% | 601128 | All Buildings | MEP
36 | 23 33 50 | Fire / Smoke Dampers | 600 | EA | 850 | 10% | 580635 | All Buildings | MEP
37 | 23 21 60 | CHW/HW Valves, Expansion Tanks & Air Separators | 1 | LS | 850000 | 10% | 967725 | All Buildings | MEP
38 | 23 31 50 | Ductwork — Galvanized Supply / Return / Exhaust — breakdown ↓ | 484438.6277 | LB | 9 | 10% | 4963800.3991 | All Buildings | MEP
| 23 31 51 | • Ductwork — Sheet Metal | 0 | LS | 2615968.5898 | 10% | 0 | All Buildings | MEP
| 23 31 52 | • Ductwork — Fittings & Dampers | 0 | LS | 1089986.9124 | 10% | 0 | All Buildings | MEP
| 23 31 53 | • Ductwork — Hangers & Sealing | 0 | LS | 653992.1475 | 10% | 0 | All Buildings | MEP
39 | 23 07 50 | Duct & Pipe Insulation — Mechanical | 180000 | SF | 4 | 10% | 819720 | All Buildings | MEP
40 | 23 05 50 | Mechanical Seismic Restraints & Hangers | 1 | LS | 650000 | 10% | 740025 | All Buildings | MEP
41 | 23 05 93 | Testing, Adjusting & Balancing (TAB) | 1 | LS | 480000 | 10% | 546480 | All Buildings | MEP
42 | 23 63 00 | Dry Coolers / Fluid Coolers — Free Cooling | 8550 | TON | 185 | 10% | 1800822.375 | All Buildings | MEP
43 | 23 09 60 | Mechanical Leak Detection — Chilled Water & Under-Floor | 440000 | SF | 0.45 | 10% | 225423 | All Buildings | MEP
44 | 23 05 80 | Mechanical Equipment Vibration Isolation | 90 | MW | 4500 | 10% | 461092.5 | All Buildings | MEP
45 | 23 21 70 | CW/CHW Pipe Freeze Protection / Heat Trace | 12000 | LF | 22 | 10% | 300564 | All Buildings | MEP
46 | 23 31 60 | Acoustic Louvers & Sound Attenuation | 90 | MW | 3500 | 10% | 358627.5 | All Buildings | MEP
|  | Subtotal — HVAC / COOLING SYSTEMS |  |  |  |  | 226484248.0019
DIVISION 25 — INTEGRATED AUTOMATION | [8 empty] | MEP
1 | 25 05 00 | Integrated Automation Common Work — OT Cabling & Pathways | 800000 | SF | 0.8 | 10% | 728640 | All Buildings | MEP
2 | 25 10 00 | Integrated Automation Network — OT Backbone (Switches, Fiber, Segmentation) | 1 | LS | 1500000 | 10% | 1707750 | All Buildings | MEP
3 | 25 11 00 | Integration Servers, Historian & Operator Workstations | 12 | EA | 32000 | 10% | 437184 | All Buildings | MEP
4 | 25 13 00 | Integration Control Panels — Tie-In / Aggregation (IACP) | 45 | EA | 12000 | 10% | 614790 | All Buildings | MEP
5 | 25 14 00 | Protocol Gateways / Routers (BACnet / Modbus / SNMP) | 36 | EA | 8000 | 10% | 327888 | All Buildings | MEP
6 | 25 30 00 | Master Systems Integrator (MSI) — Engineering & Point Mapping — breakdown ↓ | 90 | MW | 35000 | 10% | 3586275 | All Buildings | MEP
| 25 30 01 | • MSI — Design | 0 | LS | 945000 | 10% | 0 | All Buildings | MEP
| 25 30 02 | • MSI — Integration | 0 | LS | 1417500 | 10% | 0 | All Buildings | MEP
| 25 30 03 | • MSI — Test & Commission | 0 | LS | 787500 | 10% | 0 | All Buildings | MEP
7 | 25 50 00 | Facility Controls Integration — BMS / EPMS / DCIM — breakdown ↓ | 1 | LS | 2000000 | 10% | 2277000 | All Buildings | MEP
| 25 50 01 | • Facility Controls — Integration | 0 | LS | 1000000 | 10% | 0 | All Buildings | MEP
| 25 50 02 | • Facility Controls — Programming | 0 | LS | 600000 | 10% | 0 | All Buildings | MEP
| 25 50 03 | • Facility Controls — Testing | 0 | LS | 400000 | 10% | 0 | All Buildings | MEP
8 | 25 55 00 | Fire Alarm / Security Integration to Automation | 1 | LS | 550000 | 10% | 626175 | All Buildings | MEP
9 | 25 90 00 | Sequence of Operations Development & Controls Programming — breakdown ↓ | 90 | MW | 22000 | 10% | 2254230 | All Buildings | MEP
| 25 90 01 | • SOO — Development | 0 | LS | 990000 | 10% | 0 | All Buildings | MEP
| 25 90 02 | • SOO — Documentation | 0 | LS | 495000 | 10% | 0 | All Buildings | MEP
| 25 90 03 | • SOO — Validation | 0 | LS | 495000 | 10% | 0 | All Buildings | MEP
10 | 25 95 00 | Integration Testing, Tuning & Cx Support | 1 | LS | 800000 | 10% | 910800 | All Buildings | MEP
|  | Subtotal — INTEGRATED AUTOMATION |  |  |  |  | 13470732
DIVISION 26 — ELECTRICAL / CRITICAL POWER | [8 empty] | MEP
1 | 26 05 00 | Electrical Common Work — Conduit, Wire, Supports — breakdown ↓ | 800000 | SF | 5.6 | 10% | 5100480 | All Buildings | MEP
| 26 05 01 | • Common Work — Conduit & Raceway | 0 | LS | 2464000 | 10% | 0 | All Buildings | MEP
| 26 05 02 | • Common Work — Wire & Cable | 0 | LS | 1344000 | 10% | 0 | All Buildings | MEP
| 26 05 03 | • Common Work — Boxes & Fittings | 0 | LS | 672000 | 10% | 0 | All Buildings | MEP
2 | 26 05 10 | Grounding & Bonding System | 440000 | SF | 1.5 | 10% | 751410 | All Buildings | MEP
3 | 26 05 20 | Lightning Protection System | 800000 | SF | 1 | 10% | 910800 | All Buildings | MEP
4 | 26 06 00 | Medium Voltage Switchgear (15kV / 35kV) — breakdown ↓ | 9 | EA | 250000 | 10% | 2561625 | All Buildings | MEP
| 26 06 01 | • MV Switchgear — Gear | 0 | LS | 1530000 | 10% | 0 | All Buildings | MEP
| 26 06 02 | • MV Switchgear — Breakers | 0 | LS | 450000 | 10% | 0 | All Buildings | MEP
| 26 06 03 | • MV Switchgear — Install & Testing | 0 | LS | 270000 | 10% | 0 | All Buildings | MEP
5 | 26 06 10 | Medium Voltage Cable — Utility to Switchgear — breakdown ↓ | 18000 | LF | 175 | 10% | 3586275 | All Buildings | MEP
| 26 06 11 | • MV Cable — Cable | 0 | LS | 2047500 | 10% | 0 | All Buildings | MEP
| 26 06 12 | • MV Cable — Terminations | 0 | LS | 630000 | 10% | 0 | All Buildings | MEP
| 26 06 13 | • MV Cable — Testing | 0 | LS | 472500 | 10% | 0 | All Buildings | MEP
6 | 26 09 00 | Power Monitoring & Metering System (EPMS) | 1800 | PT | 500 | 10% | 1024650 | All Buildings | MEP
7 | 26 11 00 | Utility Transformers — MV to LV — breakdown ↓ | 108000 | kVA | 25 | 10% | 3073950 | All Buildings | MEP
| 26 11 01 | • Transformers — Units | 0 | LS | 1890000 | 10% | 0 | All Buildings | MEP
| 26 11 02 | • Transformers — Pads & Install | 0 | LS | 405000 | 10% | 0 | All Buildings | MEP
| 26 11 03 | • Transformers — Testing | 0 | LS | 405000 | 10% | 0 | All Buildings | MEP
8 | 26 11 10 | Transformers — UPS Input / Output — breakdown ↓ | 99000 | kVA | 24.5 | 10% | 2761431.75 | All Buildings | MEP
| 26 11 11 | • UPS Input Xfmr — Units | 0 | LS | 1697850 | 10% | 0 | All Buildings | MEP
| 26 11 12 | • UPS Input Xfmr — Install | 0 | LS | 363825 | 10% | 0 | All Buildings | MEP
| 26 11 13 | • UPS Input Xfmr — Testing | 0 | LS | 363825 | 10% | 0 | All Buildings | MEP
9 | 26 11 20 | Dry-Type Transformers — PDU / RPP — breakdown ↓ | 94500 | kVA | 21 | 10% | 2259353.25 | All Buildings | MEP
| 26 11 21 | • Dry-Type Xfmr — Units | 0 | LS | 1389150 | 10% | 0 | All Buildings | MEP
| 26 11 22 | • Dry-Type Xfmr — Install | 0 | LS | 297675 | 10% | 0 | All Buildings | MEP
| 26 11 23 | • Dry-Type Xfmr — Testing | 0 | LS | 297675 | 10% | 0 | All Buildings | MEP
10 | 26 12 00 | Main Switchboards — 480V — breakdown ↓ | 30 | EA | 245000 | 10% | 8367975 | All Buildings | MEP
| 26 12 01 | • Switchboards — Units | 0 | LS | 4998000 | 10% | 0 | All Buildings | MEP
| 26 12 02 | • Switchboards — Breakers & Metering | 0 | LS | 1470000 | 10% | 0 | All Buildings | MEP
| 26 12 03 | • Switchboards — Install & Terminations | 0 | LS | 882000 | 10% | 0 | All Buildings | MEP
11 | 26 13 00 | Automatic Transfer Switches (ATS) — breakdown ↓ | 45 | EA | 52500 | 10% | 2689706.25 | All Buildings | MEP
| 26 13 01 | • ATS — Units | 0 | LS | 1606500 | 10% | 0 | All Buildings | MEP
| 26 13 02 | • ATS — Install | 0 | LS | 401625 | 10% | 0 | All Buildings | MEP
| 26 13 03 | • ATS — Testing | 0 | LS | 354375 | 10% | 0 | All Buildings | MEP
12 | 26 14 00 | Distribution Panelboards — Mechanical — breakdown ↓ | 360 | EA | 17500 | 10% | 7172550 | All Buildings | MEP
| 26 14 01 | • Panelboards (Mech) — Boards | 0 | LS | 3906000 | 10% | 0 | All Buildings | MEP
| 26 14 02 | • Panelboards (Mech) — Breakers | 0 | LS | 1386000 | 10% | 0 | All Buildings | MEP
| 26 14 03 | • Panelboards (Mech) — Install | 0 | LS | 1008000 | 10% | 0 | All Buildings | MEP
13 | 26 14 10 | Distribution Panelboards — Lighting / General — breakdown ↓ | 720 | EA | 8400 | 10% | 6885648 | All Buildings | MEP
| 26 14 11 | • Panelboards (Lighting) — Boards | 0 | LS | 3628800 | 10% | 0 | All Buildings | MEP
| 26 14 12 | • Panelboards (Lighting) — Breakers | 0 | LS | 1330560 | 10% | 0 | All Buildings | MEP
| 26 14 13 | • Panelboards (Lighting) — Install | 0 | LS | 1088640 | 10% | 0 | All Buildings | MEP
14 | 26 20 00 | Standby Generators — Diesel (2MW+) — breakdown ↓ | 112500 | kW | 200 | 10% | 25616250 | All Buildings | MEP
| 26 20 01 | • Generators — Diesel Gensets | 0 | LS | 13500000 | 10% | 0 | All Buildings | MEP
| 26 20 02 | • Generators — Fuel Day Tanks, Exhaust & Silencers | 0 | LS | 3375000 | 10% | 0 | All Buildings | MEP
| 26 20 03 | • Generators — Paralleling Switchgear & Controls | 0 | LS | 3375000 | 10% | 0 | All Buildings | MEP
| 26 20 04 | • Generators — Install, Rigging & Commissioning | 0 | LS | 2250000 | 10% | 0 | All Buildings | MEP
15 | 26 20 10 | Generator Paralleling Switchgear — breakdown ↓ | 112500 | kW | 70 | 10% | 8965687.5 | All Buildings | MEP
| 26 20 11 | • Paralleling Switchgear — Gear | 0 | LS | 4882500 | 10% | 0 | All Buildings | MEP
| 26 20 12 | • Paralleling Switchgear — Controls & Sync | 0 | LS | 1575000 | 10% | 0 | All Buildings | MEP
| 26 20 13 | • Paralleling Switchgear — Install & Commissioning | 0 | LS | 1417500 | 10% | 0 | All Buildings | MEP
16 | 26 20 20 | Generator Exhaust / Silencer System — breakdown ↓ | 56.25 | EA | 52500 | 10% | 3362132.8125 | All Buildings | MEP
| 26 20 21 | • Gen Exhaust — Silencers | 0 | LS | 1624218.75 | 10% | 0 | All Buildings | MEP
| 26 20 22 | • Gen Exhaust — Exhaust Piping | 0 | LS | 885937.5 | 10% | 0 | All Buildings | MEP
| 26 20 23 | • Gen Exhaust — Supports & Install | 0 | LS | 442968.75 | 10% | 0 | All Buildings | MEP
17 | 26 20 30 | Generator Fuel Day Tanks — breakdown ↓ | 56.25 | EA | 45500 | 10% | 2913848.4375 | All Buildings | MEP
| 26 20 31 | • Day Tanks — Tanks | 0 | LS | 1535625 | 10% | 0 | All Buildings | MEP
| 26 20 32 | • Day Tanks — Piping & Pumps | 0 | LS | 639843.75 | 10% | 0 | All Buildings | MEP
| 26 20 33 | • Day Tanks — Controls & Leak Detection | 0 | LS | 383906.25 | 10% | 0 | All Buildings | MEP
18 | 26 20 40 | Generator Enclosures / Sound Attenuation — breakdown ↓ | 56.25 | EA | 87500 | 10% | 5603554.6875 | All Buildings | MEP
| 26 20 41 | • Gen Enclosures — Enclosures | 0 | LS | 3051562.5 | 10% | 0 | All Buildings | MEP
| 26 20 42 | • Gen Enclosures — Sound Attenuation | 0 | LS | 1230468.75 | 10% | 0 | All Buildings | MEP
| 26 20 43 | • Gen Enclosures — Install | 0 | LS | 639843.75 | 10% | 0 | All Buildings | MEP
19 | 26 21 00 | Generator Load Banks (Testing) | 3 | EA | 175000 | 10% | 597712.5 | All Buildings | MEP
20 | 26 30 00 | Uninterruptible Power Supply (UPS) — Static — breakdown ↓ | 90000 | kW | 250 | 10% | 25616250 | All Buildings | MEP
| 26 30 01 | • UPS — Modules | 0 | LS | 12375000 | 10% | 0 | All Buildings | MEP
| 26 30 02 | • UPS — Battery Systems | 0 | LS | 5625000 | 10% | 0 | All Buildings | MEP
| 26 30 03 | • UPS — Input/Output Switchgear | 0 | LS | 2700000 | 10% | 0 | All Buildings | MEP
| 26 30 04 | • UPS — Install & Commissioning | 0 | LS | 1800000 | 10% | 0 | All Buildings | MEP
21 | 26 30 10 | UPS Batteries — VRLA / Lithium-Ion — breakdown ↓ | 90000 | kW | 100 | 10% | 10246500 | All Buildings | MEP
| 26 30 12 | • UPS Batteries — Cells / Strings | 0 | LS | 6300000 | 10% | 0 | All Buildings | MEP
| 26 30 13 | • UPS Batteries — Racks / Cabinets | 0 | LS | 1350000 | 10% | 0 | All Buildings | MEP
| 26 30 14 | • UPS Batteries — Monitoring (BMS) | 0 | LS | 900000 | 10% | 0 | All Buildings | MEP
| 26 30 15 | • UPS Batteries — Install | 0 | LS | 450000 | 10% | 0 | All Buildings | MEP
22 | 26 30 20 | UPS Maintenance Bypass — External | 27000 | kW | 52.5 | 10% | 1613823.75 | All Buildings | MEP
23 | 26 31 00 | Static Transfer Switch (STS) — breakdown ↓ | 360 | EA | 25000 | 10% | 10246500 | All Buildings | MEP
| 26 31 01 | • STS — Units | 0 | LS | 6300000 | 10% | 0 | All Buildings | MEP
| 26 31 02 | • STS — Enclosures & Bypass | 0 | LS | 1620000 | 10% | 0 | All Buildings | MEP
| 26 31 03 | • STS — Install & Terminations | 0 | LS | 1080000 | 10% | 0 | All Buildings | MEP
24 | 26 32 00 | Power Distribution Units (PDU) — breakdown ↓ | 720 | EA | 35000 | 10% | 28690200 | All Buildings | MEP
| 26 32 01 | • PDU — Units | 0 | LS | 15624000 | 10% | 0 | All Buildings | MEP
| 26 32 02 | • PDU — Output Distribution Panels & Breakers | 0 | LS | 4536000 | 10% | 0 | All Buildings | MEP
| 26 32 03 | • PDU — Monitoring & Metering | 0 | LS | 2520000 | 10% | 0 | All Buildings | MEP
| 26 32 04 | • PDU — Install & Terminations | 0 | LS | 2520000 | 10% | 0 | All Buildings | MEP
25 | 26 32 10 | Remote Power Panels (RPP) — breakdown ↓ | 360 | EA | 24500 | 10% | 10041570 | All Buildings | MEP
| 26 32 11 | • RPP — Panels | 0 | LS | 5733000 | 10% | 0 | All Buildings | MEP
| 26 32 12 | • RPP — Branch Breakers | 0 | LS | 1764000 | 10% | 0 | All Buildings | MEP
| 26 32 13 | • RPP — Monitoring & Install | 0 | LS | 1323000 | 10% | 0 | All Buildings | MEP
26 | 26 33 00 | Overhead Busway — Data Hall — breakdown ↓ | 88000 | LF | 150 | 10% | 15028200 | All Buildings | MEP
| 26 33 01 | • Busway — Runs | 0 | LS | 8580000 | 10% | 0 | All Buildings | MEP
| 26 33 02 | • Busway — Supports & Hangers | 0 | LS | 1980000 | 10% | 0 | All Buildings | MEP
| 26 33 03 | • Busway — Connections & Terminations | 0 | LS | 2640000 | 10% | 0 | All Buildings | MEP
27 | 26 33 10 | Busway Tap-Off Boxes — breakdown ↓ | 3600 | EA | 2450 | 10% | 10041570 | All Buildings | MEP
| 26 33 11 | • Tap-Off Boxes — Units | 0 | LS | 6174000 | 10% | 0 | All Buildings | MEP
| 26 33 12 | • Tap-Off Boxes — Breakers | 0 | LS | 1587600 | 10% | 0 | All Buildings | MEP
| 26 33 13 | • Tap-Off Boxes — Install | 0 | LS | 1058400 | 10% | 0 | All Buildings | MEP
28 | 26 34 00 | Whips & Connections — Cabinet Level — breakdown ↓ | 8800 | EA | 250 | 10% | 2504700 | All Buildings | MEP
| 26 34 01 | • Whips — Whips | 0 | LS | 1320000 | 10% | 0 | All Buildings | MEP
| 26 34 02 | • Whips — Connectors | 0 | LS | 550000 | 10% | 0 | All Buildings | MEP
| 26 34 03 | • Whips — Install | 0 | LS | 330000 | 10% | 0 | All Buildings | MEP
29 | 26 40 00 | Interior Lighting — Office / Support | 120000 | SF | 4.2 | 10% | 573804 | All Buildings | MEP
30 | 26 40 10 | Interior Lighting — Data Halls (LED) — breakdown ↓ | 440000 | SF | 5.6 | 10% | 2805264 | All Buildings | MEP
| 26 40 11 | • Interior Lighting — Fixtures | 0 | LS | 1478400 | 10% | 0 | All Buildings | MEP
| 26 40 12 | • Interior Lighting — Controls & Sensors | 0 | LS | 492800 | 10% | 0 | All Buildings | MEP
| 26 40 13 | • Interior Lighting — Install & Wiring | 0 | LS | 492800 | 10% | 0 | All Buildings | MEP
31 | 26 40 20 | Emergency / Egress Lighting | 800000 | SF | 0.7 | 10% | 637560 | All Buildings | MEP
32 | 26 41 00 | Exterior Lighting — Building Mounted | 40000 | SF | 5.6 | 10% | 255024 | All Buildings | MEP
33 | 26 42 00 | Lighting Controls — Occupancy / Daylighting | 800000 | SF | 1.05 | 10% | 956340 | All Buildings | MEP
34 | 26 50 00 | Surge Protection Devices (SPD) | 30 | EA | 10500 | 10% | 358627.5 | All Buildings | MEP
35 | 26 51 00 | Arc Flash Mitigation — Relay Protection — breakdown ↓ | 180 | EA | 10500 | 10% | 2151765 | All Buildings | MEP
| 26 51 01 | • Arc Flash — Relays | 0 | LS | 1039500 | 10% | 0 | All Buildings | MEP
| 26 51 02 | • Arc Flash — Settings & Study | 0 | LS | 472500 | 10% | 0 | All Buildings | MEP
| 26 51 03 | • Arc Flash — Install | 0 | LS | 378000 | 10% | 0 | All Buildings | MEP
36 | 26 52 00 | Power Factor Correction Capacitors | 90 | EA | 17500 | 10% | 1793137.5 | All Buildings | MEP
37 | 26 53 00 | Electrical Testing & Commissioning — breakdown ↓ | 90 | MW | 35000 | 10% | 3586275 | All Buildings | MEP
| 26 53 01 | • Elec Cx — L1-2 Startup | 0 | LS | 1102500 | 10% | 0 | All Buildings | MEP
| 26 53 02 | • Elec Cx — L3 Functional | 0 | LS | 945000 | 10% | 0 | All Buildings | MEP
| 26 53 03 | • Elec Cx — L4-5 Integrated | 0 | LS | 1102500 | 10% | 0 | All Buildings | MEP
38 | 26 27 50 | Motor Control Centers — Mechanical — breakdown ↓ | 24 | EA | 85000 | 10% | 2322540 | All Buildings | MEP
| 26 27 51 | • MCC — Units | 0 | LS | 1326000 | 10% | 0 | All Buildings | MEP
| 26 27 52 | • MCC — Breakers / Starters | 0 | LS | 448800 | 10% | 0 | All Buildings | MEP
| 26 27 53 | • MCC — Install | 0 | LS | 265200 | 10% | 0 | All Buildings | MEP
39 | 26 05 60 | Feeder Cable & Terminations — LV — breakdown ↓ | 60554.8285 | LF | 85 | 10% | 5860042.1379 | All Buildings | MEP
| 26 05 61 | • LV Feeder — Cable | 0 | LS | 3088296.2518 | 10% | 0 | All Buildings | MEP
| 26 05 62 | • LV Feeder — Terminations | 0 | LS | 1286790.1049 | 10% | 0 | All Buildings | MEP
| 26 05 63 | • LV Feeder — Testing | 0 | LS | 772074.063 | 10% | 0 | All Buildings | MEP
40 | 26 32 50 | Battery Energy Storage (BESS) Tie-In — breakdown ↓ | 1 | LS | 2800000 | 10% | 3187800 | All Buildings | MEP
| 26 32 51 | • BESS — Battery Racks | 0 | LS | 1540000 | 10% | 0 | All Buildings | MEP
| 26 32 52 | • BESS — PCS / Inverters | 0 | LS | 700000 | 10% | 0 | All Buildings | MEP
| 26 32 53 | • BESS — Controls & Install | 0 | LS | 560000 | 10% | 0 | All Buildings | MEP
41 | 26 05 36 | Cable Tray & Wireway Systems — Electrical | 24000 | LF | 65 | 10% | 1776060 | All Buildings | MEP
42 | 26 27 60 | Wiring Devices & Receptacles | 4800 | EA | 95 | 10% | 519156 | All Buildings | MEP
43 | 26 05 26 | Grounding & Bonding — Electrical Ground Grid | 1 | LS | 850000 | 10% | 967725 | All Buildings | MEP
44 | 26 41 01 | Lightning Protection System | 1 | LS | 350000 | 10% | 398475 | All Buildings | MEP
45 | 26 05 73 | Arc-Flash & Coordination Study | 1 | LS | 180000 | 10% | 204930 | All Buildings | MEP
46 | 26 51 50 | Emergency & Egress Lighting | 1800 | EA | 280 | 10% | 573804 | All Buildings | MEP
47 | 26 05 19 | Medium-Voltage Distribution — Building Unit Substations | 9 | EA | 185000 | 10% | 1895602.5 | All Buildings | MEP
48 | 26 05 48 | Electrical Equipment Seismic Anchorage & Bracing | 90 | MW | 6500 | 10% | 666022.5 | All Buildings | MEP
49 | 26 05 53 | Electrical Identification & Arc-Flash Labeling | 800000 | SF | 0.15 | 10% | 136620 | All Buildings | MEP
50 | 26 05 90 | Temporary Construction Power & Distribution | 90 | MW | 12000 | 10% | 1229580 | All Buildings | MEP
51 | 26 05 99 | Electrical Spare Parts & Maintenance Stock | 90 | MW | 4500 | 10% | 461092.5 | All Buildings | MEP
52 | 26 20 50 | Generator Radiators / Remote Cooling Systems | 56.25 | EA | 35000 | 10% | 2241421.875 | All Buildings | MEP
53 | 26 20 60 | Generator Fuel Polishing / Filtration System | 56.25 | EA | 18000 | 10% | 1152731.25 | All Buildings | MEP
54 | 26 20 70 | Generator Emissions Control (SCR / Tier 4) | 112500 | kW | 25 | 10% | 3202031.25 | All Buildings | MEP
|  | Subtotal — ELECTRICAL / CRITICAL POWER |  |  |  |  | 248147784.9504
DIVISION 27 — COMMUNICATIONS / IT INFRASTRUCTURE | [8 empty] | MEP
1 | 27 05 00 | Pathway & Spaces — Cable Tray, Ladder Rack, J-Hooks | 45000 | LF | 35 | 10% | 1793137.5 | All Buildings | MEP
2 | 27 05 10 | Firestopping — Communications Penetrations | 5625 | EA | 245 | 10% | 1568995.3125 | All Buildings | MEP
3 | 27 10 00 | Structured Cabling — Cat6A (Data Halls) | 4400 | DROP | 200 | 10% | 1001880 | All Buildings | MEP
4 | 27 10 10 | Structured Cabling — Cat6A (Office / Support) | 600 | DROP | 245 | 10% | 167359.5 | All Buildings | MEP
5 | 27 11 00 | Fiber Optic Cabling — Single Mode Backbone | 90000 | LF | 5 | 10% | 512325 | All Buildings | MEP
6 | 27 11 10 | Fiber Optic Cabling — Multi-Mode Distribution | 45000 | LF | 5.6 | 10% | 286902 | All Buildings | MEP
7 | 27 13 00 | Main Distribution Area (MDA) Buildout | 3 | EA | 175000 | 10% | 597712.5 | All Buildings | MEP
8 | 27 13 10 | Intermediate Distribution Area (IDA) | 8.8 | EA | 70000 | 10% | 701316 | All Buildings | MEP
9 | 27 15 00 | IT Cabinets & Racks — 42U / 52U — breakdown ↓ | 4400 | EA | 2500 | 10% | 12523500 | All Buildings | MEP
| 27 15 01 | • IT Racks — Cabinets / Racks | 0 | LS | 7150000 | 10% | 0 | All Buildings | MEP
| 27 15 02 | • IT Racks — Rack PDUs / Power Strips | 0 | LS | 2200000 | 10% | 0 | All Buildings | MEP
| 27 15 03 | • IT Racks — Containment & Accessories | 0 | LS | 1650000 | 10% | 0 | All Buildings | MEP
10 | 27 15 10 | Cabinet Accessories — PDU Strips, Blanking Panels — breakdown ↓ | 4440.6874 | EA | 1050 | 10% | 5308508.7601 | All Buildings | MEP
| 27 15 11 | • Cabinet Accessories — Blanking Panels | 0 | LS | 1865088.7167 | 10% | 0 | All Buildings | MEP
| 27 15 12 | • Cabinet Accessories — Cable Management | 0 | LS | 1631952.6271 | 10% | 0 | All Buildings | MEP
| 27 15 13 | • Cabinet Accessories — Grounding & Hardware | 0 | LS | 1165680.448 | 10% | 0 | All Buildings | MEP
11 | 27 16 00 | Overhead Cable Management — Waterfall Trays | 220000 | SF | 1.4 | 10% | 350658 | All Buildings | MEP
12 | 27 20 00 | Fiber Patch Panels & Enclosures — breakdown ↓ | 4400 | EA | 3150 | 10% | 15779610 | All Buildings | MEP
| 27 20 01 | • Fiber — Panels & Enclosures | 0 | LS | 6930000 | 10% | 0 | All Buildings | MEP
| 27 20 02 | • Fiber — Cassettes / Modules | 0 | LS | 4158000 | 10% | 0 | All Buildings | MEP
| 27 20 03 | • Fiber — Terminations & Testing | 0 | LS | 2772000 | 10% | 0 | All Buildings | MEP
13 | 27 21 00 | Copper Patch Panels — breakdown ↓ | 4400 | EA | 1050 | 10% | 5259870 | All Buildings | MEP
| 27 21 01 | • Copper Panels — Panels | 0 | LS | 2541000 | 10% | 0 | All Buildings | MEP
| 27 21 02 | • Copper Panels — Jacks & Modules | 0 | LS | 1386000 | 10% | 0 | All Buildings | MEP
| 27 21 03 | • Copper Panels — Terminations & Testing | 0 | LS | 693000 | 10% | 0 | All Buildings | MEP
14 | 27 30 00 | DCIM — Data Center Infrastructure Management | 4400 | CAB | 150 | 10% | 751410 | All Buildings | MEP
15 | 27 31 00 | Environmental Monitoring — Temp / Humidity Sensors | 4400 | EA | 245 | 10% | 1227303 | All Buildings | MEP
16 | 27 32 00 | Water Leak Detection System — Under Raised Floor — breakdown ↓ | 444068.7421 | LF | 10 | 10% | 5055722.6287 | All Buildings | MEP
| 27 32 01 | • Leak Detection — Sensing Cable | 0 | LS | 2220343.7105 | 10% | 0 | All Buildings | MEP
| 27 32 02 | • Leak Detection — Controllers | 0 | LS | 1332206.2263 | 10% | 0 | All Buildings | MEP
| 27 32 03 | • Leak Detection — Integration & Install | 0 | LS | 888137.4842 | 10% | 0 | All Buildings | MEP
17 | 27 40 00 | Audio / Visual System — NOC / SOC | 1 | LS | 245000 | 10% | 278932.5 | All Buildings | MEP
18 | 27 41 00 | Audio / Visual — Conference Rooms | 12 | EA | 17500 | 10% | 239085 | All Buildings | MEP
19 | 27 50 00 | Wireless Access Points (WAP) | 320 | EA | 1750 | 10% | 637560 | All Buildings | MEP
20 | 27 60 00 | Telecom Entrance Facility — Meet-Me Room | 3 | EA | 175000 | 10% | 597712.5 | All Buildings | MEP
21 | 27 51 00 | Distributed Antenna System (DAS) — Cellular | 1 | LS | 850000 | 10% | 967725 | All Buildings | MEP
22 | 27 52 00 | Public Address / Intercom | 1 | LS | 280000 | 10% | 318780 | All Buildings | MEP
23 | 27 05 60 | Telecom Bonding & Grounding (TBB/TGB) | 1 | LS | 280000 | 10% | 318780 | All Buildings | MEP
24 | 27 53 00 | Two-Way Radio / BDA Coverage System | 1 | LS | 650000 | 10% | 740025 | All Buildings | MEP
25 | 27 32 50 | Master Clock / Timing Distribution | 1 | LS | 220000 | 10% | 250470 | All Buildings | MEP
26 | 27 21 50 | KVM / Console Management — Data Halls | 1 | LS | 480000 | 10% | 546480 | All Buildings | MEP
27 | 27 05 28 | Telecom Pathways — Innerduct & Sleeves | 40000 | LF | 12 | 10% | 546480 | All Buildings | MEP
28 | 27 08 00 | Communications Commissioning & Acceptance Testing | 90 | MW | 3500 | 10% | 358627.5 | All Buildings | MEP
29 | 27 10 50 | Pre-Terminated MPO/MTP Trunk Cabling | 4400 | EA | 145 | 10% | 726363 | All Buildings | MEP
30 | 27 11 50 | Campus / OSP Fiber Backbone — Inter-Building (SM) | 24000 | LF | 18 | 10% | 491832 | All Buildings | MEP
31 | 27 13 50 | Horizontal Distribution Area (HDA) Buildout | 36 | EA | 12500 | 10% | 512325 | All Buildings | MEP
|  | Subtotal — COMMUNICATIONS / IT INFRASTRUCTURE |  |  |  |  | 60417387.7013
DIVISION 28 — ELECTRONIC SAFETY & SECURITY | [8 empty] | MEP
1 | 28 05 00 | Security Common Work — Conduit & Wiring | 800000 | SF | 1.05 | 10% | 956340 | All Buildings | MEP
2 | 28 10 00 | Access Control System — Card Reader / Biometric | 320 | EA | 3500 | 10% | 1275120 | All Buildings | MEP
3 | 28 10 10 | Access Control — Mantrap / Interlock Vestibule — breakdown ↓ | 160 | EA | 35000 | 10% | 6375600 | All Buildings | MEP
| 28 10 11 | • Mantrap — Interlock Doors & Controllers | 0 | LS | 2800000 | 10% | 0 | All Buildings | MEP
| 28 10 12 | • Mantrap — Readers & Biometrics | 0 | LS | 1400000 | 10% | 0 | All Buildings | MEP
| 28 10 13 | • Mantrap — Integration & Software | 0 | LS | 840000 | 10% | 0 | All Buildings | MEP
| 28 10 14 | • Mantrap — Install | 0 | LS | 560000 | 10% | 0 | All Buildings | MEP
4 | 28 10 20 | Access Control — Vehicle Gate Integration | 8 | EA | 24500 | 10% | 223146 | All Buildings | MEP
5 | 28 13 00 | CCTV / Video Surveillance — Interior | 400 | EA | 2500 | 10% | 1138500 | All Buildings | MEP
6 | 28 13 10 | CCTV / Video Surveillance — Exterior | 80 | EA | 5950 | 10% | 541926 | All Buildings | MEP
7 | 28 13 20 | Video Management System (VMS) & Storage | 1 | LS | 525000 | 10% | 597712.5 | All Buildings | MEP
8 | 28 15 00 | Intrusion Detection — Perimeter Fence | 3577.7088 | LF | 24.5 | 10% | 99793.925 | All Buildings | MEP
9 | 28 15 10 | Intrusion Detection — Interior Motion / Glass Break | 400 | EA | 595 | 10% | 270963 | All Buildings | MEP
10 | 28 16 00 | Security Operations Center (SOC) Buildout | 1 | LS | 595000 | 10% | 677407.5 | All Buildings | MEP
11 | 28 17 00 | Visitor Management System | 1 | LS | 52500 | 10% | 59771.25 | All Buildings | MEP
12 | 28 18 00 | Guard Booth — Vehicle Checkpoint | 3 | EA | 87500 | 10% | 298856.25 | All Buildings | MEP
13 | 28 20 00 | Security Monitoring & Alarm Integration | 1 | LS | 245000 | 10% | 278932.5 | All Buildings | MEP
14 | 28 23 00 | Vehicle Barrier System — Crash Rated | 12 | EA | 15000 | 10% | 204930 | All Buildings | MEP
15 | 28 30 00 | Security Lighting — IR / White Light | 100 | EA | 1050 | 10% | 119542.5 | All Buildings | MEP
16 | 28 13 50 | Optical Turnstiles — Lobby | 24 | EA | 28000 | 10% | 765072 | All Buildings | MEP
17 | 28 16 50 | Duress / Panic Alarm System | 1 | LS | 280000 | 10% | 318780 | All Buildings | MEP
18 | 28 13 60 | Weapons / Package Screening — Lobby | 1 | LS | 280000 | 10% | 318780 | All Buildings | MEP
19 | 28 16 60 | Rising Bollards — Vehicle Sally Port | 12 | EA | 45000 | 10% | 614790 | All Buildings | MEP
20 | 28 23 50 | Video Analytics / AI Surveillance Platform | 90 | MW | 2500 | 10% | 256162.5 | All Buildings | MEP
21 | 28 13 70 | Visitor Management System | 9 | EA | 35000 | 10% | 358627.5 | All Buildings | MEP
|  | Subtotal — ELECTRONIC SAFETY & SECURITY |  |  |  |  | 15750753.425
DIVISION 31 — EARTHWORK | [8 empty] | CSA
1 | 31 10 00 | Site Clearing & Demolition | 1200000 | SF | 1.5 | 10% | 2049300 | Shared | CSA
2 | 31 22 00 | Grading & Excavation | 14814.8148 | CY | 8 | 10% | 134933.3333 | Shared | CSA
3 | 31 23 00 | Fill, Backfill & Compaction | 11851.8519 | CY | 12 | 10% | 161920 | Shared | CSA
4 | 31 23 10 | Structural Fill — Under Slabs | 14814.8148 | CY | 22 | 10% | 371066.6667 | Shared | CSA
5 | 31 25 00 | Erosion & Sediment Control | 1200000 | SF | 0.15 | 10% | 204930 | Shared | CSA
6 | 31 31 00 | Soil Treatment / Stabilization | 80000 | SF | 1.5 | 10% | 136620 | Shared | CSA
7 | 31 40 00 | Shoring & Underpinning | 40000 | SF | 17.5 | 10% | 796950 | Shared | CSA
8 | 31 50 00 | Excavation Support — Sheet Piling | 40000 | SF | 24.5 | 10% | 1115730 | Shared | CSA
9 | 31 62 00 | Driven Piles — breakdown ↓ | 240000 | LF | 35 | 10% | 9563400 | Shared | CSA
| 31 62 01 | • Driven Piles — Pile Material | 0 | LS | 4200000 | 10% | 0 | Shared | CSA
| 31 62 02 | • Driven Piles — Driving & Equipment | 0 | LS | 2940000 | 10% | 0 | Shared | CSA
| 31 62 03 | • Driven Piles — Testing & PDA | 0 | LS | 840000 | 10% | 0 | Shared | CSA
| 31 62 04 | • Driven Piles — Cutoffs & Prep | 0 | LS | 420000 | 10% | 0 | Shared | CSA
10 | 31 63 00 | Drilled Shafts (Caissons) — breakdown ↓ | 40000 | LF | 140 | 10% | 6375600 | Shared | CSA
| 31 63 01 | • Drilled Shafts — Drilling | 0 | LS | 2800000 | 10% | 0 | Shared | CSA
| 31 63 02 | • Drilled Shafts — Concrete & Rebar | 0 | LS | 1680000 | 10% | 0 | Shared | CSA
| 31 63 03 | • Drilled Shafts — Casing | 0 | LS | 672000 | 10% | 0 | Shared | CSA
| 31 63 04 | • Drilled Shafts — Testing | 0 | LS | 448000 | 10% | 0 | Shared | CSA
11 | 31 23 20 | Dewatering — Construction | 1 | LS | 350000 | 10% | 398475 | Shared | CSA
12 | 31 05 13 | Aggregate Base Course — Under Slab/Paving | 18000 | CY | 38 | 10% | 778734 | Shared | CSA
13 | 31 32 00 | Geotextile / Soil Stabilization Fabric | 600000 | SF | 0.6 | 10% | 409860 | Shared | CSA
14 | 31 23 30 | Rock Excavation & Blasting | 8000 | CY | 65 | 10% | 592020 | Shared | CSA
15 | 31 23 40 | Surplus Soil Export & Haul-Off | 60000 | CY | 14 | 10% | 956340 | Shared | CSA
16 | 31 11 50 | Temporary Construction Roads & Laydown | 1 | LS | 600000 | 10% | 683100 | Shared | CSA
17 | 31 22 50 | Topsoil Stripping & Stockpiling | 22000 | CY | 8 | 10% | 200376 | Shared | CSA
18 | 31 22 60 | Fine Grading & Subgrade Preparation | 800000 | SF | 0.4 | 10% | 364320 | Shared | CSA
19 | 31 25 50 | SWPPP & Construction Fence | 1 | LS | 180000 | 10% | 204930 | Shared | CSA
20 | 31 09 00 | Geotechnical Instrumentation & Monitoring | 12 | EA | 8500 | 10% | 116127 | All Buildings | CSA
|  | Subtotal — EARTHWORK |  |  |  |  | 25614732
DIVISION 32 — EXTERIOR IMPROVEMENTS | [8 empty] | CSA
1 | 32 12 00 | Flexible Paving — Asphalt | 400000 | SF | 3.5 | 10% | 1593900 | Shared | CSA
2 | 32 13 00 | Rigid Paving — Concrete | 120000 | SF | 7 | 10% | 956340 | Shared | CSA
3 | 32 16 00 | Curbs & Gutters | 3577.7088 | LF | 35 | 10% | 142562.75 | Shared | CSA
4 | 32 17 00 | Parking Lot Striping & Signage | 400000 | SF | 0.35 | 10% | 159390 | Shared | CSA
5 | 32 31 00 | Security Fencing — 8' Chain Link + Barbed Wire | 3577.7088 | LF | 45 | 10% | 183294.9643 | Shared | CSA
6 | 32 31 10 | Perimeter Bollards — K-Rated | 100 | EA | 3500 | 10% | 398475 | Shared | CSA
7 | 32 32 00 | Vehicle Gates — Slide / Swing | 8 | EA | 52500 | 10% | 478170 | Shared | CSA
8 | 32 84 00 | Irrigation System | 160000 | SF | 1.05 | 10% | 191268 | Shared | CSA
9 | 32 90 00 | Landscaping | 240000 | SF | 2.8 | 10% | 765072 | Shared | CSA
10 | 32 11 00 | Sidewalks & Pedestrian Paving | 40000 | SF | 8 | 10% | 364320 | Shared | CSA
11 | 32 32 50 | Retaining Walls — Site | 12000 | SF | 45 | 10% | 614790 | Shared | CSA
12 | 32 17 50 | Guard Rails & Crash Barriers — Site | 3500 | LF | 55 | 10% | 219161.25 | Shared | CSA
13 | 32 13 50 | Heavy-Duty Concrete Hardstand — Equipment Yard | 90000 | SF | 14 | 10% | 1434510 | Shared | CSA
14 | 32 12 50 | Truck Court & Dock Apron Paving | 60000 | SF | 9 | 10% | 614790 | Shared | CSA
15 | 32 17 60 | Parking Bumpers & Wheel Stops | 600 | EA | 65 | 10% | 44401.5 | Shared | CSA
16 | 32 84 50 | Site Stormwater — Inlets, Manholes & Catch Basins | 120 | EA | 3200 | 10% | 437184 | Shared | CSA
17 | 32 31 50 | Security Gates & Crash-Rated Barriers (K-Rated) | 8 | EA | 85000 | 10% | 774180 | All Buildings | CSA
|  | Subtotal — EXTERIOR IMPROVEMENTS |  |  |  |  | 9371809.4642
DIVISION 33 — UTILITIES | [8 empty] | CSA
1 | 33 10 00 | Water Distribution — Main Connection | 1 | LS | 75000 | 10% | 85387.5 | Shared | CSA
2 | 33 30 00 | Sanitary Sewer — Main Connection | 1 | LS | 140000 | 10% | 159390 | Shared | CSA
3 | 33 40 00 | Storm Drainage System — breakdown ↓ | 800000 | SF | 2.5 | 10% | 2277000 | Shared | CSA
| 33 40 01 | • Storm Drainage — Piping | 0 | LS | 1100000 | 10% | 0 | Shared | CSA
| 33 40 02 | • Storm Drainage — Structures (Inlets/MH) | 0 | LS | 600000 | 10% | 0 | Shared | CSA
| 33 40 03 | • Storm Drainage — Install | 0 | LS | 300000 | 10% | 0 | Shared | CSA
4 | 33 41 00 | Stormwater Detention / Retention | 80000 | SF | 5.6 | 10% | 510048 | Shared | CSA
5 | 33 50 10 | Fuel Oil Distribution — Generator Farm — breakdown ↓ | 112500 | LF | 105 | 10% | 13448531.25 | Shared | CSA
| 33 50 11 | • Fuel — Day Tanks & Bulk Piping | 0 | LS | 5315625 | 10% | 0 | Shared | CSA
| 33 50 12 | • Fuel — Pumps, Filtration & Polishing | 0 | LS | 2953125 | 10% | 0 | Shared | CSA
| 33 50 13 | • Fuel — Controls & Leak Detection | 0 | LS | 1771875 | 10% | 0 | Shared | CSA
| 33 50 14 | • Fuel — Install & Testing | 0 | LS | 1771875 | 10% | 0 | Shared | CSA
6 | 33 51 00 | Fuel Storage Tanks — Above Ground — breakdown ↓ | 1687500 | GAL | 1.5 | 10% | 2881828.125 | Shared | CSA
| 33 51 01 | • Fuel Tanks — Tanks | 0 | LS | 1569375 | 10% | 0 | Shared | CSA
| 33 51 02 | • Fuel Tanks — Foundations & Containment | 0 | LS | 582187.5 | 10% | 0 | Shared | CSA
| 33 51 03 | • Fuel Tanks — Install & Testing | 0 | LS | 379687.5 | 10% | 0 | Shared | CSA
7 | 33 52 00 | Fuel Oil Piping & Fill Station — breakdown ↓ | 56250 | LF | 140 | 10% | 8965687.5 | Shared | CSA
| 33 52 01 | • Fuel Piping — Piping & Fittings | 0 | LS | 4331250 | 10% | 0 | Shared | CSA
| 33 52 02 | • Fuel Piping — Fill Station & Pumps | 0 | LS | 1968750 | 10% | 0 | Shared | CSA
| 33 52 03 | • Fuel Piping — Supports & Insulation | 0 | LS | 945000 | 10% | 0 | Shared | CSA
| 33 52 04 | • Fuel Piping — Testing | 0 | LS | 630000 | 10% | 0 | Shared | CSA
8 | 33 71 00 | Electrical Utility — Primary Service Entrance — breakdown ↓ | 90 | MW | 250000 | 10% | 25616250 | Shared | CSA
| 33 71 01 | • Utility Substation & Transformers | 0 | LS | 10125000 | 10% | 0 | Shared | CSA
| 33 71 02 | • Primary Feeders & Duct Bank | 0 | LS | 5625000 | 10% | 0 | Shared | CSA
| 33 71 03 | • Metering & Protection Relays | 0 | LS | 3375000 | 10% | 0 | Shared | CSA
| 33 71 04 | • Utility Coordination & Switchgear | 0 | LS | 3375000 | 10% | 0 | Shared | CSA
9 | 33 71 10 | Utility Ductbank — Medium Voltage — breakdown ↓ | 9000 | LF | 350 | 10% | 3586275 | Shared | CSA
| 33 71 11 | • MV Ductbank — Excavation & Conduit | 0 | LS | 1575000 | 10% | 0 | Shared | CSA
| 33 71 12 | • MV Ductbank — Concrete Encasement | 0 | LS | 945000 | 10% | 0 | Shared | CSA
| 33 71 13 | • MV Ductbank — Manholes | 0 | LS | 630000 | 10% | 0 | Shared | CSA
10 | 33 73 00 | Utility Metering — Revenue Grade | 90 | EA | 17500 | 10% | 1793137.5 | Shared | CSA
11 | 33 79 00 | Site Lighting — LED Poles & Fixtures | 100 | EA | 3150 | 10% | 358627.5 | Shared | CSA
12 | 33 82 00 | Fiber Optic Utility Entrance — Diverse Path | 1 | LS | 175000 | 10% | 199237.5 | Shared | CSA
13 | 33 52 50 | Natural Gas Service & Distribution | 4200 | LF | 85 | 10% | 406444.5 | Shared | CSA
14 | 33 82 50 | Communications Ductbank — Site | 9000 | LF | 140 | 10% | 1434510 | Shared | CSA
15 | 33 12 50 | Domestic Water Booster Pump Station | 2 | EA | 180000 | 10% | 409860 | Shared | CSA
16 | 33 31 50 | Sanitary Lift Station | 1 | LS | 350000 | 10% | 398475 | Shared | CSA
17 | 33 09 50 | Utility SCADA / Monitoring | 1 | LS | 280000 | 10% | 318780 | Shared | CSA
18 | 33 05 50 | Utility Trenching, Bedding & Backfill | 18000 | LF | 28 | 10% | 573804 | Shared | CSA
19 | 33 46 00 | Subdrainage / Under-Slab Drainage System | 440000 | SF | 0.35 | 10% | 175329 | All Buildings | CSA
|  | Subtotal — UTILITIES |  |  |  |  | 63598602.375
|  | SUBTOTAL (All Divisions) |  |  |  |  | 1088341827.0674
|  | Contingency |  |  | 10% |  | (included in line items)
|  | TOTAL PROJECT BUDGET |  |  |  |  | 1088341827.0674
|  | Cost per MW: |  |  |  |  | 12092686.9674
|  | Cost per SF: |  |  |  |  | 1360.4273
|  | Cost per Watt: |  |  |  |  | 12.0927
UNIT COST DATABASE — TIE-OUT CHECK
|  | Active pricing tier (live, from database) |  |  | Low
|  | CSI line items priced from database |  |  | 747
|  | Codes not found in database (should be 0) |  |  | 0
|  | Σ all line items = grand total (no orphans / double-counts) |  |  | ✅ Ties
|  | Tie-out status — all line prices sourced from Unit Cost Database |  |  | ✅ Tied
Note on D341: Kevin: Alternate — not selected in base design (clean-agent/pre-action carries the base scope). Qty set to 0; no cost carried. Set qty + unit price if this alternate is accepted.
Note on D438: Kevin: Not used — project uses hot-aisle containment (see containment line above). Qty set to 0; no cost carried.
Note on D507: Kevin: LS scope carried on parent line (facility controls integration). Component split retained below as $0 memo.
Note on D617: Corrected qty basis: 2 power whips per cabinet (A+B feeds). Cabinets = raised-floor SF / 100. Prior formula (=$C$13) counted one whip per SF of raised floor (~440,000), a unit/quantity mismatch that overstated this line by ~$260M.
Note on D618: Corrected qty basis: 2 power whips per cabinet (A+B feeds). Cabinets = raised-floor SF / 100. Prior formula (=$C$13) counted one whip per SF of raised floor (~440,000), a unit/quantity mismatch that overstated this line by ~$260M.
Note on D619: Corrected qty basis: 2 power whips per cabinet (A+B feeds). Cabinets = raised-floor SF / 100. Prior formula (=$C$13) counted one whip per SF of raised floor (~440,000), a unit/quantity mismatch that overstated this line by ~$260M.
Note on D620: Corrected qty basis: 2 power whips per cabinet (A+B feeds). Cabinets = raised-floor SF / 100. Prior formula (=$C$13) counted one whip per SF of raised floor (~440,000), a unit/quantity mismatch that overstated this line by ~$260M.
Note on D647: Kevin: LS scope carried on parent line (BESS tie-in is integration scope). Component split retained below as $0 memo.
Note on F27: Unit cost from Unit Cost Database (SC 09 00, $7,500/MW). Prior manual override removed after DB unit corrected from % to MW.
Note on H9: Kevin: Linked to F3 (Estimate Date) so all sheets reference one source of truth.

## Campus Rollup
DATA CENTER CAMPUS — PROGRAM-LEVEL ROLLUP
Program Name: | Data Center Template, Northern Virginia |  | Client: | Confidential Hyperscaler |  | Estimate Class: | Class 3 (DD)
Location: | Loudoun County, VA |  | Estimate Date: | 2026-05-01 |  | Accuracy Range: | −20% / +30%
BUILDING-BY-BUILDING SUMMARY
# | Building | GBA (SF) | IT Load (MW) | CSA Cost | MEP Cost | Other (Cx/GC/Soft) | Total | $/SF | $/MW
1 | Building 1 (B1) | 250000 | 30 | 59235638.009 | 203053666.0325 | 15789097.5 | 278078401.5414 | 1112.3136 | 9269280.0514
2 | Building 2 (B2) | 250000 | 30 | 59235638.009 | 203053666.0325 | 15789097.5 | 278078401.5414 | 1112.3136 | 9269280.0514
3 | Building 3 (B3) | 250000 | 30 | 59235638.009 | 203053666.0325 | 15789097.5 | 278078401.5414 | 1112.3136 | 9269280.0514
4 | Building 4 (B4) | 0 | 0 | 0 | 0 | 0 | 0 | — | —
5 | Building 5 (B5) | 0 | 0 | 0 | 0 | 0 | 0 | — | —
6 | Building 6 (B6) | 0 | 0 | 0 | 0 | 0 | 0 | — | —
S | Shared Infrastructure | 50000 | 0 | 98025001.8392 | 0 | 156081620.6039 | 254106622.4431 | — | —
| CAMPUS TOTAL | 800000 | 90 | 275731915.8661 | 609160998.0974 | 203448913.1039 | 1088341827.0674 | 1360.4273 | 12092686.9674
PROGRAM-LEVEL METRICS
CSA Share of Total: | 25.34% |  | MEP Share of Total: | 55.97% |  | Other Share: | 18.69%
Campus $/SF (excl. Shared): | 1112.3136 |  | Campus $/MW (incl. Shared): | 12092686.9674 |  | Cost per Watt: | 12.0927
PROGRAM ECONOMICS — ALL-IN (bridge to TDC)
Hard construction (this tab): | 1088341827.0674 |  | All-in development cost: | 1512873780.308 |  | Hard cost % of all-in: | 71.94%
Construction $/MW: | 12092686.9674 |  | All-in $/MW: | 16809708.6701 |  | Capex uplift $/MW: | 4717021.7027
Construction $/SF (incl. shared): | 1360.4273 |  | All-in $/SF: | 1891.0922 |  | All-in cost per Watt: | 16.8097
Senior loan (60% LTC): | 907724268.1848 |  | Sponsor equity: | 605149512.1232 |  | Loan-to-cost: | 60%
NOTES
• Tag each Construction Budget line in column I (Building) to one of B1–B6 or "Shared" so it rolls up here.
• Column J (Scope) auto-classifies CSA / MEP / Cx / GC / Soft based on division. Override per line if needed.
• Shared Infrastructure = site-wide utilities, security perimeter, central plant, common roads — not allocated to a specific building.
• Campus $/SF excludes Shared Infra (which has no allocable SF). Campus $/MW includes Shared (allocated against total IT load).
— chart source data —
CSA (core & shell) | 275731915.8661
MEP (power & cooling) | 609160998.0974
Other (Cx / GC / soft) | 203448913.1039
Note on B7: Buildings 1-3 are identical 250K SF / 30 MW units; CSA/MEP/Cx allocations pull from 'All Buildings' tagged lines in Construction Budget and divide by 3.
Note on F7: MEP now multiplied by the active MEP config factor (Scenario & Presets!B67) so redundancy and rack density drive cost. Baseline N+1/High = 1.00.

## CSA Summary
CIVIL / STRUCTURAL / ARCHITECTURAL (CSA) ESTIMATE SUMMARY
Scope: | Civil + Structural + Architectural (excludes MEP, Cx, GC, Soft Costs)
CSA DIVISION | Base (current) | Hyperscale (Hybrid) | Air-Cooled | AI / HPC (Liquid)
Earthwork (Div 31) | 25614732 | 38723329.7478 | 38723329.7478 | 57459743.4219
Exterior Improvements (Div 32) | 9371809.4642 | 14167927.5902 | 14167927.5902 | 21023127.1291
Utilities (Div 33) | 63598602.375 | 96145829.3325 | 96145829.3325 | 142666313.06
Concrete (Div 03) | 33466040.3876 | 50592624.482 | 50592624.482 | 75072036.4366
Metals / Structural Steel (Div 05) | 40836399.762 | 61734839.689 | 61734839.689 | 91605450.0432
Thermal & Moisture (Div 07) | 38165650.875 | 57697308.091 | 57697308.091 | 85614345.167
Openings (Div 08) | 13742209.9774 | 20774924.6964 | 20774924.6964 | 30826942.064
Finishes (Div 09) | 33189552 | 50174640.3702 | 50174640.3702 | 74451809.3029
Specialties (Div 10) | 4010233.425 | 6062510.8739 | 6062510.8739 | 8995877.2031
Masonry (Div 04) | 5656068 | 8550617.9116 | 8550617.9116 | 12687863.2209
Wood, Plastics & Composites (Div 06) | 1233678.6 | 1865026.0807 | 1865026.0807 | 2767425.2388
Equipment (Div 11) | 1525590 | 2306326.0873 | 2306326.0873 | 3422249.7416
Furnishings (Div 12) | 1217056.5 | 1839897.4532 | 1839897.4532 | 2730138.0401
Conveying Equipment (Div 14) | 4104292.5 | 6204705.6303 | 6204705.6303 | 9206873.3719
TOTAL CSA | 275731915.8661 | 416840508.0361 | 416840508.0361 | 618530193.4411
Hyperscale / Air-Cooled / AI-HPC = Base division mix scaled to each scenario's CSA total (Scenario Comparison) — indicative, not separately estimated.
CSA UNIT METRICS
GBA (SF) | 800000 | 800000 | 800000 | 800000
CSA $/SF | 344.6649 | 521.0506 | 521.0506 | 773.1627
CSA IN CONTEXT
Total CSA cost | 275731915.8661
Campus CSA $/SF (blended) | 344.6649
CSA % of total construction | 25.34%
CSA % of all-in TDC | 18.23%
— chart source data —
Earthwork (Div 31) | 25614732
Exterior Improvements (Div 32) | 9371809.4642
Utilities (Div 33) | 63598602.375
Concrete (Div 03) | 33466040.3876
Metals / Structural Steel (Div 05) | 40836399.762
Thermal & Moisture (Div 07) | 38165650.875
Openings (Div 08) | 13742209.9774
Finishes (Div 09) | 33189552
Specialties (Div 10) | 4010233.425
Masonry (Div 04) | 5656068
Wood, Plastics & Composites (Div 06) | 1233678.6
Equipment (Div 11) | 1525590
Furnishings (Div 12) | 1217056.5
Conveying Equipment (Div 14) | 4104292.5

## Unit Cost Database
DATA CENTER — UNIT COST DATABASE / STANDARD REFERENCE PRICING | [6 empty] | Pricing Tier: | Low
CSI Code | Description | Unit | Low Range | Mid Range | High Range | Notes | Selected Price
31 10 00 | Site Clearing & Demolition | SF | 1.5 | 2.5 | 4 | Per SF of site area; varies with existing conditions | 1.5
31 22 00 | Grading & Excavation | CY | 8 | 15 | 25 | Per cubic yard; rock excavation at high end | 8
31 23 00 | Fill, Backfill & Compaction | CY | 12 | 22 | 35 | Includes import fill, placement, and proof-roll | 12
31 62 00 | Driven Piles | LF | 35 | 55 | 85 | Per LF of pile; steel H-pile typical | 35
32 12 00 | Asphalt Paving | SF | 3.5 | 5.5 | 8 | 4" HMA over 8" aggregate base | 3.5
32 13 00 | Concrete Paving | SF | 7 | 11 | 16 | 6" reinforced concrete; truck aprons higher | 7
32 31 00 | Security Fencing — 8' Chain Link + Barbed Wire | LF | 45 | 75 | 120 | Per LF including gates; K-rated bollards separate | 45
33 10 00 | Water Distribution — Main Connection | LS | 75000 | 150000 | 300000 | Tap, meter, backflow, site distribution | 75000
33 40 00 | Storm Drainage System | SF | 2.5 | 5 | 9 | Per SF of site; includes detention/retention | 2.5
33 50 00 | Fuel Oil Distribution — Generator Farm | GAL | 3 | 5.5 | 8.5 | Per gallon of storage capacity; AST w/ piping | 3
33 71 00 | Electrical Utility — Primary Service Entrance | MW | 250000 | 450000 | 750000 | Per MW; includes ductbank, switchgear pad, metering | 250000
03 30 00 | Cast-in-Place Concrete — Foundations | CY | 450 | 650 | 950 | Per CY placed; includes form, rebar, finish | 450
03 30 30 | Slab on Grade — Data Halls (FF/FL) | SF | 10 | 16 | 24 | 6"+ slab w/ vapor barrier; FF50/FL25 min | 10
03 40 00 | Precast Concrete — Tilt-Up Panels | SF | 18 | 28 | 42 | Per SF of panel face; erected and sealed | 18
05 12 00 | Structural Steel Framing | TON | 3500 | 5000 | 7500 | Fabricated and erected; connections included | 3500
05 31 00 | Steel Decking — Roof | SF | 4.5 | 7 | 10 | 1.5" Type B; installed on steel joists | 4.5
07 41 00 | Metal Wall Panels — Insulated | SF | 18 | 28 | 42 | IMPs; R-25+ typical for data centers | 18
07 52 00 | Single-Ply Membrane Roofing (TPO/EPDM) | SF | 8 | 13 | 20 | Fully adhered; includes insulation and walkway pads | 8
07 84 00 | Firestopping / Penetration Sealing | EA | 35 | 75 | 150 | Per penetration; UL-listed systems | 35
22 10 00 | Domestic Water — Plumbing Fixtures | FIX | 2500 | 4500 | 7000 | Per fixture; includes rough-in and trim | 2500
22 15 00 | Make-Up Water — Cooling Towers | GPM | 800 | 1500 | 2500 | Per GPM capacity; RO/DI treatment included | 800
22 30 00 | Acid Neutralization Tank — Battery Room | EA | 15000 | 35000 | 60000 | Per tank; VRLA acid neutralization typical | 15000
21 13 00 | Pre-Action Sprinkler System — Data Halls | SF | 6 | 10 | 16 | Double interlock pre-action; per SF protected | 6
21 22 00 | Clean Agent System — FM-200 / Novec 1230 | SF | 12 | 22 | 35 | Per SF of protected zone; includes tanks and piping | 12
21 30 00 | VESDA Detection | SF | 3 | 6 | 10 | Per SF; aspirating smoke detection | 3
21 31 00 | Fire Alarm / Mass Notification System | SF | 4 | 7 | 12 | Per SF total building; FACP, devices, wiring | 4
21 35 00 | Fire Pump | EA | 60000 | 100000 | 175000 | Per pump; electric or diesel drive | 60000
23 21 00 | Centrifugal Chillers — Water-Cooled | TON | 800 | 1200 | 1800 | Per ton; 500-2000 ton units typical | 800
23 22 00 | Cooling Towers — Induced Draft | TON | 200 | 350 | 550 | Per ton; includes basin, VFDs, piping | 200
23 21 20 | Chilled Water Piping — Primary Loop | LF | 80 | 150 | 250 | Per LF; 8"-16" welded steel insulated | 80
23 23 00 | CRAH Units | TON | 600 | 950 | 1400 | Per ton; chilled water CRAHs, 30-100 ton units | 600
23 24 00 | Hot/Cold Aisle Containment | CAB | 800 | 1500 | 2500 | Per cabinet position; panels, doors, roof | 800
23 25 00 | Economizer System — Waterside | TON | 100 | 200 | 350 | Per ton; plate-and-frame HX, controls | 100
23 09 00 | Building Management System (BMS) | PT | 350 | 600 | 950 | Per point; includes controllers, sensors, programming | 350
23 60 00 | Direct Liquid Cooling Infrastructure | kW | 150 | 300 | 500 | Per kW; CDUs, manifolds, piping to racks | 150
26 06 00 | Medium Voltage Switchgear (15kV/35kV) | EA | 250000 | 450000 | 750000 | Per lineup; includes breakers, relays, testing | 250000
26 11 00 | Utility Transformers — MV to LV | kVA | 25 | 45 | 70 | Per kVA; 2000-3000 kVA units typical | 25
26 20 00 | Standby Generators — Diesel (2MW+) | kW | 200 | 350 | 550 | Per kW; includes paralleling, enclosure, exhaust | 200
26 30 00 | UPS — Static (Rotary higher) | kW | 250 | 450 | 700 | Per kW; 500kW-1.5MW modules; double-conversion | 250
26 30 10 | UPS Batteries — VRLA | kW | 100 | 175 | 275 | Per kW supported; 10-15 min runtime | 100
26 30 11 | UPS Batteries — Lithium-Ion | kW | 175 | 300 | 475 | Per kW; longer life, smaller footprint vs VRLA | 175
26 31 00 | Static Transfer Switch (STS) | EA | 25000 | 50000 | 85000 | Per unit; 100A-4000A range | 25000
26 32 00 | Power Distribution Units (PDU) | EA | 35000 | 65000 | 110000 | Per unit; 75-500 kVA; transformer + breakers | 35000
26 33 00 | Overhead Busway — Data Hall | LF | 150 | 275 | 450 | Per LF; 225A-800A; includes tap-off boxes | 150
26 34 00 | Whips & Connections — Cabinet Level | EA | 250 | 500 | 850 | Per drop; A+B feeds typical | 250
26 05 10 | Grounding & Bonding System | SF | 1.5 | 3 | 5 | Per SF data hall; ground grid, risers, bonds | 1.5
26 05 20 | Lightning Protection System | SF | 1 | 2 | 3.5 | Per SF roof area; air terminals, conductors, grounds | 1
26 09 00 | Power Monitoring (EPMS) | PT | 500 | 850 | 1300 | Per metering point; includes software/dashboard | 500
08 11 00 | Hollow Metal Doors & Frames | EA | 1200 | 2000 | 3200 | Per opening; includes hardware | 1200
08 33 00 | Overhead Coiling Doors — Loading Dock | EA | 8000 | 14000 | 22000 | Per door; 10'x12' insulated typical | 8000
09 69 00 | Raised Access Floor — Data Halls | SF | 22 | 35 | 55 | Per SF; 24"+ height; 2500lb concentrated load | 22
09 96 00 | Epoxy Flooring — Battery / Mech Rooms | SF | 6 | 10 | 16 | Chemical-resistant; includes surface prep | 6
09 21 00 | Gypsum Board — Interior Partitions | SF | 6 | 10 | 16 | Per SF of wall; both sides; studs included | 6
27 05 00 | Cable Tray & Ladder Rack | LF | 35 | 65 | 110 | Per LF; 12"-24" wide; includes supports | 35
27 10 00 | Structured Cabling — Cat6A | DROP | 200 | 350 | 550 | Per drop; includes patch panel, testing, labeling | 200
27 11 00 | Fiber Optic Cabling — SM Backbone | LF | 5 | 10 | 18 | Per LF of 48-strand SM; terminated both ends | 5
27 15 00 | IT Cabinets & Racks — 42U/52U | EA | 2500 | 5000 | 8500 | Per cabinet; includes seismic bracing | 2500
27 30 00 | DCIM — Infrastructure Management Software | CAB | 150 | 300 | 500 | Per cabinet monitored; license + sensors | 150
27 32 00 | Water Leak Detection — Under Raised Floor | LF | 10 | 18 | 30 | Per LF of sensing cable; controller separate | 10
28 10 00 | Access Control — Card Reader / Biometric | EA | 3500 | 6000 | 10000 | Per controlled opening; includes panel share | 3500
28 10 10 | Mantrap / Interlock Vestibule | EA | 35000 | 65000 | 110000 | Per vestibule; doors, readers, interlock logic | 35000
28 13 00 | CCTV / Video Surveillance | EA | 2500 | 4500 | 7500 | Per camera position; includes VMS share | 2500
28 23 00 | Vehicle Barrier — Crash Rated (K-rated) | EA | 15000 | 35000 | 65000 | Per barrier; K4-K12 rating range | 15000
CX 01 00 | Commissioning Management & Administration | MW | 50000 | 100000 | 175000 | Per MW IT load; overall Cx program mgmt | 50000
CX 06 00 | Integrated Systems Testing (IST) | MW | 75000 | 150000 | 275000 | Per MW; load banks, fuel, labor | 75000
01 10 00 | General Conditions — Project Management | MO | 80000 | 135000 | 200000 | Per month; PM, super, safety, QC staff | 80000
01 50 00 | Temporary Facilities — Site Office | MO | 20000 | 40000 | 65000 | Per month; trailers, utilities, IT | 20000
SC 01 00 | A/E Design Fees | % | 0.04 | 0.06 | 0.09 | As % of hard costs; MEP-heavy scope | 0.04
SC 09 00 | Third-Party CxA | MW | 7500 | 8625 | 10125 | Third-party CxA / Owner's CxA; $/MW basis (corrected from %). | 7500
SC 10 00 | Uptime Institute Tier Certification | EA | 75000 | 150000 | 250000 | Per facility; TCDD + TCCF; Tier III-IV | 75000
SC 15 00 | BIM / Virtual Design & Construction | % | 0.005 | 0.01 | 0.02 | As % of hard costs; LOD 300-400 | 0.005
— | Data Center — All-In Cost per MW | MW | 8000000 | 12000000 | 18000000 | Total project cost per MW IT; Tier III benchmark
31 40 00 | Shoring & Underpinning | SF | 17.5 | 25 | 35 | Seeded from CB hardcode | 17.5
31 50 00 | Excavation Support — Sheet Piling | SF | 24.5 | 35 | 49 | Seeded from CB hardcode | 24.5
31 63 00 | Drilled Shafts (Caissons) | LF | 140 | 200 | 280 | Seeded from CB hardcode | 140
32 16 00 | Curbs & Gutters | LF | 35 | 50 | 70 | Seeded from CB hardcode | 35
32 17 00 | Parking Lot Striping & Signage | SF | 0.35 | 0.5 | 0.7 | Seeded from CB hardcode | 0.35
32 31 10 | Perimeter Bollards — K-Rated | EA | 3500 | 5000 | 7000 | Seeded from CB hardcode | 3500
32 32 00 | Vehicle Gates — Slide / Swing | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
32 84 00 | Irrigation System | SF | 1.05 | 1.5 | 2.1 | Seeded from CB hardcode | 1.05
32 90 00 | Landscaping | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
33 30 00 | Sanitary Sewer — Main Connection | LS | 140000 | 200000 | 280000 | Seeded from CB hardcode | 140000
33 41 00 | Stormwater Detention / Retention | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
33 50 10 | Fuel Oil Distribution — Generator Farm | LF | 105 | 150 | 210 | Seeded from CB hardcode | 105
33 52 00 | Fuel Oil Piping & Fill Station | LF | 140 | 200 | 280 | Seeded from CB hardcode | 140
33 71 10 | Utility Ductbank — Medium Voltage | LF | 350 | 500 | 700 | Seeded from CB hardcode | 350
33 73 00 | Utility Metering — Revenue Grade | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
33 79 00 | Site Lighting — LED Poles & Fixtures | EA | 3150 | 4500 | 6300 | Seeded from CB hardcode | 3150
33 82 00 | Fiber Optic Utility Entrance — Diverse Path | LS | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
03 35 00 | Concrete Finishing — Data Hall Floor Flatness (FF/FL) | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
03 41 00 | Precast Structural Members | SF | 21 | 30 | 42 | Seeded from CB hardcode | 21
03 05 00 | Concrete Accessories — Embeds, Anchors | SF | 0.35 | 0.5 | 0.7 | Seeded from CB hardcode | 0.35
05 12 10 | Structural Steel — Mezzanine / Elevated Platforms | TON | 3850 | 5500 | 7700 | Seeded from CB hardcode | 3850
05 12 20 | Structural Steel — Generator / Equipment Support | TON | 3850 | 5500 | 7700 | Seeded from CB hardcode | 3850
05 21 00 | Steel Joists | SF | 4.2 | 6 | 8.4 | Seeded from CB hardcode | 4.2
05 40 00 | Cold-Formed Metal Framing | SF | 8.4 | 12 | 16.8 | Seeded from CB hardcode | 8.4
05 50 00 | Metal Fabrications — Stairs, Railings, Ladders | SF | 1.4 | 2 | 2.8 | Seeded from CB hardcode | 1.4
05 51 00 | Metal Stairs — Interior | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
05 52 00 | Pipe / Equipment Supports — Seismic Bracing | EA | 5600 | 8000 | 11200 | Seeded from CB hardcode | 5600
05 53 00 | Cable Tray / Ladder Rack Support Steel | LF | 17.5 | 25 | 35 | Seeded from CB hardcode | 17.5
07 11 00 | Dampproofing — Foundation | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
07 13 00 | Sheet Membrane Waterproofing | SF | 8.4 | 12 | 16.8 | Seeded from CB hardcode | 8.4
07 21 00 | Building Insulation — Walls | SF | 4.2 | 6 | 8.4 | Seeded from CB hardcode | 4.2
07 22 00 | Roof Insulation | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
07 42 00 | Metal Soffit Panels | SF | 17.5 | 25 | 35 | Seeded from CB hardcode | 17.5
07 51 00 | Built-Up Roofing (BUR) / Modified Bitumen | SF | 9.8 | 14 | 19.6 | Seeded from CB hardcode | 9.8
07 62 00 | Sheet Metal Flashing & Trim | SF | 1.05 | 1.5 | 2.1 | Seeded from CB hardcode | 1.05
07 71 00 | Roof Specialties — Hatches, Vents, Curbs | EA | 2800 | 4000 | 5600 | Seeded from CB hardcode | 2800
07 72 00 | Roof Accessories — Walkway Pads, Fall Protection | SF | 0.35 | 0.5 | 0.7 | Seeded from CB hardcode | 0.35
07 81 00 | Applied Fireproofing — Spray | TON | 2450 | 3500 | 4900 | Seeded from CB hardcode | 2450
07 92 00 | Joint Sealants | SF | 0.35 | 0.5 | 0.7 | Seeded from CB hardcode | 0.35
22 11 00 | Domestic Hot Water System | FIX | 3850 | 5500 | 7700 | Seeded from CB hardcode | 3850
22 13 00 | Sanitary Waste & Vent Piping | FIX | 2800 | 4000 | 5600 | Seeded from CB hardcode | 2800
22 14 00 | Storm Drainage — Interior Piping | SF | 0.84 | 1.2 | 1.68 | Seeded from CB hardcode | 0.84
22 16 00 | Condensate Drain — CRAH / AHU Units | GPM | 140 | 200 | 280 | Seeded from CB hardcode | 140
22 17 00 | Emergency Shower & Eyewash Stations | EA | 3150 | 4500 | 6300 | Seeded from CB hardcode | 3150
22 40 00 | Grease Interceptor — Kitchen / Café | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
22 50 00 | Natural Gas Piping — Generator Support | LF | 45.5 | 65 | 91 | Seeded from CB hardcode | 45.5
22 60 00 | Compressed Air System — Generator Starting | LF | 59.5 | 85 | 119 | Seeded from CB hardcode | 59.5
22 70 00 | Backflow Prevention Assemblies | EA | 8400 | 12000 | 16800 | Seeded from CB hardcode | 8400
21 05 00 | Fire Suppression — Common Work | SF | 0.35 | 0.5 | 0.7 | Seeded from CB hardcode | 0.35
21 11 00 | Wet Sprinkler System — Office / Support Areas | SF | 3.5 | 5 | 7 | Seeded from CB hardcode | 3.5
21 12 00 | Dry Sprinkler System — Loading Dock / Generator Area | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
21 32 00 | Fire Alarm Control Panels (FACP) | EA | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
21 33 00 | Smoke Evacuation / Purge System | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
21 34 00 | Standpipe System | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
21 40 00 | Fire Protection Water Storage Tank | EA | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
23 05 00 | Mechanical Common Work — Hangers, Supports, Seismic | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
23 05 10 | Mechanical Insulation | SF | 2.1 | 3 | 4.2 | Seeded from CB hardcode | 2.1
23 07 00 | HVAC Ductwork Insulation | SF | 3.5 | 5 | 7 | Seeded from CB hardcode | 3.5
23 09 10 | DCIM Integration — Environmental Monitoring | PT | 525 | 750 | 1050 | Seeded from CB hardcode | 525
23 21 10 | Chiller Plant Pumps — Primary / Secondary | EA | 105000 | 150000 | 210000 | Seeded from CB hardcode | 105000
23 21 30 | Chilled Water Piping — Secondary / Tertiary | LF | 84 | 120 | 168 | Seeded from CB hardcode | 84
23 22 10 | Condenser Water Piping | LF | 91 | 130 | 182 | Seeded from CB hardcode | 91
23 22 20 | Condenser Water Treatment System | TON | 35 | 50 | 70 | Seeded from CB hardcode | 35
23 23 10 | In-Row Cooling Units | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
23 23 20 | Rear Door Heat Exchangers (RDHx) | EA | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
23 25 10 | Economizer System — Airside | TON | 175 | 250 | 350 | Seeded from CB hardcode | 175
23 30 00 | HVAC Air Handling Units — Office / Support | SF | 12.6 | 18 | 25.2 | Seeded from CB hardcode | 12.6
23 31 00 | HVAC Ductwork — Office / Support | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
23 34 00 | HVAC Fans — Exhaust / Ventilation | EA | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
23 36 00 | Humidification System | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
23 37 00 | Air Filtration — Data Hall | SF | 3.5 | 5 | 7 | Seeded from CB hardcode | 3.5
23 38 00 | Refrigerant Piping — DX Systems | LF | 56 | 80 | 112 | Seeded from CB hardcode | 56
23 40 00 | Make-Up Water System | GPM | 420 | 600 | 840 | Seeded from CB hardcode | 420
23 50 00 | Testing, Adjusting & Balancing (TAB) | MW | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
23 65 00 | CDU — Coolant Distribution Units | EA | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
23 70 00 | Thermal Energy Storage | kWh | 560 | 800 | 1120 | Seeded from CB hardcode | 560
26 05 00 | Electrical Common Work — Conduit, Wire, Supports | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
26 06 10 | Medium Voltage Cable — Utility to Switchgear | LF | 175 | 250 | 350 | Seeded from CB hardcode | 175
26 11 10 | Transformers — UPS Input / Output | kVA | 24.5 | 35 | 49 | Seeded from CB hardcode | 24.5
26 11 20 | Dry-Type Transformers — PDU / RPP | kVA | 21 | 30 | 42 | Seeded from CB hardcode | 21
26 12 00 | Main Switchboards — 480V | EA | 245000 | 350000 | 490000 | Seeded from CB hardcode | 245000
26 13 00 | Automatic Transfer Switches (ATS) | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
26 14 00 | Distribution Panelboards — Mechanical | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
26 14 10 | Distribution Panelboards — Lighting / General | EA | 8400 | 12000 | 16800 | Seeded from CB hardcode | 8400
26 20 10 | Generator Paralleling Switchgear | kW | 70 | 100 | 140 | Seeded from CB hardcode | 70
26 20 20 | Generator Exhaust / Silencer System | EA | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
26 20 30 | Generator Fuel Day Tanks | EA | 45500 | 65000 | 91000 | Seeded from CB hardcode | 45500
26 20 40 | Generator Enclosures / Sound Attenuation | EA | 87500 | 125000 | 175000 | Seeded from CB hardcode | 87500
26 21 00 | Generator Load Banks (Testing) | EA | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
26 30 20 | UPS Maintenance Bypass — External | kW | 52.5 | 75 | 105 | Seeded from CB hardcode | 52.5
26 32 10 | Remote Power Panels (RPP) | EA | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
26 33 10 | Busway Tap-Off Boxes | EA | 2450 | 3500 | 4900 | Seeded from CB hardcode | 2450
26 40 00 | Interior Lighting — Office / Support | SF | 4.2 | 6 | 8.4 | Seeded from CB hardcode | 4.2
26 40 10 | Interior Lighting — Data Halls (LED) | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
26 40 20 | Emergency / Egress Lighting | SF | 0.7 | 1 | 1.4 | Seeded from CB hardcode | 0.7
26 41 00 | Exterior Lighting — Building Mounted | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
26 42 00 | Lighting Controls — Occupancy / Daylighting | SF | 1.05 | 1.5 | 2.1 | Seeded from CB hardcode | 1.05
26 50 00 | Surge Protection Devices (SPD) | EA | 10500 | 15000 | 21000 | Seeded from CB hardcode | 10500
26 51 00 | Arc Flash Mitigation — Relay Protection | EA | 10500 | 15000 | 21000 | Seeded from CB hardcode | 10500
26 52 00 | Power Factor Correction Capacitors | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
08 11 10 | Hollow Metal Doors & Frames — Exterior | EA | 2450 | 3500 | 4900 | Seeded from CB hardcode | 2450
08 14 00 | Acoustical Doors — Generator / Mech Rooms | EA | 5950 | 8500 | 11900 | Seeded from CB hardcode | 5950
08 31 00 | Access Doors & Panels | EA | 560 | 800 | 1120 | Seeded from CB hardcode | 560
08 34 00 | High-Speed Roll-Up Doors | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
08 36 00 | Sectional Overhead Doors | EA | 8400 | 12000 | 16800 | Seeded from CB hardcode | 8400
08 41 00 | Aluminum Entrances — Storefront | SF | 59.5 | 85 | 119 | Seeded from CB hardcode | 59.5
08 44 00 | Curtain Wall System | SF | 87.5 | 125 | 175 | Seeded from CB hardcode | 87.5
08 51 00 | Aluminum Windows | SF | 45.5 | 65 | 91 | Seeded from CB hardcode | 45.5
08 71 00 | Door Hardware — Standard | EA | 1050 | 1500 | 2100 | Seeded from CB hardcode | 1050
08 71 10 | Door Hardware — Electrified (Access Control) | EA | 2450 | 3500 | 4900 | Seeded from CB hardcode | 2450
08 80 00 | Glazing | SF | 24.5 | 35 | 49 | Seeded from CB hardcode | 24.5
08 81 00 | Security Glazing — Blast Rated | SF | 122.5 | 175 | 245 | Seeded from CB hardcode | 122.5
09 22 00 | Metal Stud Framing — Interior | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
09 51 00 | Acoustical Ceilings — Office / Support | SF | 4.2 | 6 | 8.4 | Seeded from CB hardcode | 4.2
09 65 00 | Resilient Flooring — VCT / LVT | SF | 3.5 | 5 | 7 | Seeded from CB hardcode | 3.5
09 68 00 | Carpet — Office Areas | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
09 69 20 | Raised Floor Accessories — Grommets, Ramps, Cutouts | SF | 1.4 | 2 | 2.8 | Seeded from CB hardcode | 1.4
09 72 00 | Wall Coverings — Epoxy Paint (Data Halls) | SF | 2.8 | 4 | 5.6 | Seeded from CB hardcode | 2.8
09 91 00 | Interior Painting — Standard | SF | 1.4 | 2 | 2.8 | Seeded from CB hardcode | 1.4
09 97 00 | Anti-Static / ESD Flooring — Data Halls | SF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
10 14 00 | Signage — Interior Wayfinding | EA | 1050 | 1500 | 2100 | Seeded from CB hardcode | 1050
10 14 10 | Signage — Exterior / Monument | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
10 14 20 | Safety Signage — Arc Flash / Hazmat | EA | 175 | 250 | 350 | Seeded from CB hardcode | 175
10 21 00 | Toilet Partitions | EA | 3150 | 4500 | 6300 | Seeded from CB hardcode | 3150
10 26 00 | Wall Protection — Corner Guards | LF | 24.5 | 35 | 49 | Seeded from CB hardcode | 24.5
10 28 00 | Toilet & Bath Accessories | EA | 840 | 1200 | 1680 | Seeded from CB hardcode | 840
10 44 00 | Fire Extinguishers & Cabinets | EA | 350 | 500 | 700 | Seeded from CB hardcode | 350
10 55 00 | Postal Specialties / Delivery Lockers | LS | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
10 73 00 | Protective Covers — Equipment Pads | EA | 3500 | 5000 | 7000 | Seeded from CB hardcode | 3500
10 75 00 | Flagpoles | EA | 5950 | 8500 | 11900 | Seeded from CB hardcode | 5950
27 05 10 | Firestopping — Communications Penetrations | EA | 245 | 350 | 490 | Seeded from CB hardcode | 245
27 10 10 | Structured Cabling — Cat6A (Office / Support) | DROP | 245 | 350 | 490 | Seeded from CB hardcode | 245
27 11 10 | Fiber Optic Cabling — Multi-Mode Distribution | LF | 5.6 | 8 | 11.2 | Seeded from CB hardcode | 5.6
27 13 00 | Main Distribution Area (MDA) Buildout | EA | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
27 13 10 | Intermediate Distribution Area (IDA) | EA | 70000 | 100000 | 140000 | Seeded from CB hardcode | 70000
27 15 10 | Cabinet Accessories — PDU Strips, Blanking Panels | EA | 1050 | 1500 | 2100 | Seeded from CB hardcode | 1050
27 16 00 | Overhead Cable Management — Waterfall Trays | SF | 1.4 | 2 | 2.8 | Seeded from CB hardcode | 1.4
27 20 00 | Fiber Patch Panels & Enclosures | EA | 3150 | 4500 | 6300 | Seeded from CB hardcode | 3150
27 21 00 | Copper Patch Panels | EA | 1050 | 1500 | 2100 | Seeded from CB hardcode | 1050
27 31 00 | Environmental Monitoring — Temp / Humidity Sensors | EA | 245 | 350 | 490 | Seeded from CB hardcode | 245
27 40 00 | Audio / Visual System — NOC / SOC | LS | 245000 | 350000 | 490000 | Seeded from CB hardcode | 245000
27 41 00 | Audio / Visual — Conference Rooms | EA | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
27 50 00 | Wireless Access Points (WAP) | EA | 1750 | 2500 | 3500 | Seeded from CB hardcode | 1750
27 60 00 | Telecom Entrance Facility — Meet-Me Room | EA | 175000 | 250000 | 350000 | Seeded from CB hardcode | 175000
28 05 00 | Security Common Work — Conduit & Wiring | SF | 1.05 | 1.5 | 2.1 | Seeded from CB hardcode | 1.05
28 10 20 | Access Control — Vehicle Gate Integration | EA | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
28 13 10 | CCTV / Video Surveillance — Exterior | EA | 5950 | 8500 | 11900 | Seeded from CB hardcode | 5950
28 13 20 | Video Management System (VMS) & Storage | LS | 525000 | 750000 | 1050000 | Seeded from CB hardcode | 525000
28 15 00 | Intrusion Detection — Perimeter Fence | LF | 24.5 | 35 | 49 | Seeded from CB hardcode | 24.5
28 15 10 | Intrusion Detection — Interior Motion / Glass Break | EA | 595 | 850 | 1190 | Seeded from CB hardcode | 595
28 16 00 | Security Operations Center (SOC) Buildout | LS | 595000 | 850000 | 1190000 | Seeded from CB hardcode | 595000
28 17 00 | Visitor Management System | LS | 52500 | 75000 | 105000 | Seeded from CB hardcode | 52500
28 18 00 | Guard Booth — Vehicle Checkpoint | EA | 87500 | 125000 | 175000 | Seeded from CB hardcode | 87500
28 20 00 | Security Monitoring & Alarm Integration | LS | 245000 | 350000 | 490000 | Seeded from CB hardcode | 245000
28 30 00 | Security Lighting — IR / White Light | EA | 1050 | 1500 | 2100 | Seeded from CB hardcode | 1050
01 20 00 | Price & Payment Procedures | MO | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
01 30 00 | Administrative Requirements | MO | 12600 | 18000 | 25200 | Seeded from CB hardcode | 12600
01 31 00 | Project Management Software (Procore/Primavera) | MO | 5950 | 8500 | 11900 | Seeded from CB hardcode | 5950
01 40 00 | Quality Requirements — QA/QC Program | MO | 45500 | 65000 | 91000 | Seeded from CB hardcode | 45500
01 50 10 | Temporary Utilities — Power, Water, Sanitary | MO | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
01 51 00 | Temporary Construction — Fencing, Barriers | MO | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
01 52 00 | Construction Waste Management & Recycling | MO | 24500 | 35000 | 49000 | Seeded from CB hardcode | 24500
01 54 00 | Construction Cleaning — Progress & Final | MO | 45500 | 65000 | 91000 | Seeded from CB hardcode | 45500
01 55 00 | Vehicular Access & Haul Roads | MO | 12600 | 18000 | 25200 | Seeded from CB hardcode | 12600
01 56 00 | Environmental Protection | MO | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
01 60 00 | Product Requirements — Submittals & Substitutions | MO | 12600 | 18000 | 25200 | Seeded from CB hardcode | 12600
01 70 00 | Execution & Closeout Requirements | MO | 17500 | 25000 | 35000 | Seeded from CB hardcode | 17500
01 78 00 | Closeout Submittals — As-Builts, Warranties | MO | 12600 | 18000 | 25200 | Seeded from CB hardcode | 12600
31 23 10 | Structural Fill — Under Slabs | CY | 22 | 30 | 42 | Stub — no current cost; activate when scope confirmed | 22
31 25 00 | Erosion & Sediment Control | SF | 0.15 | 0.25 | 0.4 | Stub — no current cost; activate when scope confirmed | 0.15
31 31 00 | Soil Treatment / Stabilization | SF | 1.5 | 2.5 | 4 | Stub — no current cost; activate when scope confirmed | 1.5
32 11 00 | Sidewalks & Pedestrian Paving | SF | 8 | 12 | 18 | Stub — no current cost; activate when scope confirmed | 8
33 51 00 | Fuel Storage Tanks — Above Ground | GAL | 1.5 | 2.2 | 3.2 | Stub — no current cost; activate when scope confirmed | 1.5
03 10 00 | Concrete Formwork — Foundations | CY | 220 | 300 | 410 | Stub — no current cost; activate when scope confirmed | 220
03 20 00 | Concrete Reinforcement — Rebar | CY | 240 | 330 | 450 | Stub — no current cost; activate when scope confirmed | 240
03 30 10 | Cast-in-Place — Equipment Pads (Generator, Chiller, Transformer) | CY | 650 | 850 | 1100 | Stub — no current cost; activate when scope confirmed | 650
03 30 20 | Cast-in-Place — Elevated Slabs | SF | 14 | 20 | 28 | Stub — no current cost; activate when scope confirmed | 14
03 30 40 | Cast-in-Place — Loading Dock / Ramps | SF | 18 | 26 | 36 | Stub — no current cost; activate when scope confirmed | 18
05 31 10 | Steel Decking — Elevated Floors | SF | 6 | 9 | 13 | Stub — no current cost; activate when scope confirmed | 6
21 13 10 | Pre-Action Sprinkler — Electrical Rooms | SF | 5 | 7.5 | 11 | Stub — no current cost; activate when scope confirmed | 5
21 22 10 | Clean Agent System — Novec 1230 (Alternate) | LS | 0 | 0 | 0 | Stub — no current cost; activate when scope confirmed | 0
21 22 20 | Clean Agent — UPS / Battery Rooms | SF | 22 | 32 | 45 | Stub — no current cost; activate when scope confirmed | 22
21 30 10 | Smoke Detection — Duct / Plenum Detectors | SF | 0.6 | 1 | 1.6 | Stub — no current cost; activate when scope confirmed | 0.6
23 24 10 | Cold Aisle Containment System | LS | 0 | 0 | 0 | Stub — no current cost; activate when scope confirmed | 0
26 53 00 | Electrical Testing & Commissioning | MW | 35000 | 55000 | 85000 | Stub — no current cost; activate when scope confirmed | 35000
09 69 10 | Raised Access Floor — Electrical Rooms | SF | 28 | 38 | 52 | Stub — no current cost; activate when scope confirmed | 28
01 73 00 | Permits, Fees & Inspections | LS | 0 | 0 | 0 | Stub — no current cost; activate when scope confirmed | 0
01 74 00 | Bonds — Performance & Payment | LS | 0 | 0 | 0 | Stub — no current cost; activate when scope confirmed | 0
01 76 00 | Insurance — Builder's Risk, Wrap-Up | LS | 0 | 0 | 0 | Stub — no current cost; activate when scope confirmed | 0
04 05 00 | Masonry Common Work — Mortar, Grout & Reinforcing | LS | 180000 | 250000 | 340000 | Mortar, grout, joint reinforcing, ties across CMU scope | 180000
04 20 00 | CMU — Fire-Rated Walls (Electrical / UPS / Battery Rooms) | SF | 22 | 28 | 36 | 2-hr rated assemblies enclosing critical rooms; per SF of wall | 22
04 20 10 | CMU — Generator Yard Screen Walls | SF | 26 | 32 | 42 | Acoustic/visual screen at generator farm | 26
04 22 00 | Reinforced Masonry — Security / Blast-Resistant Walls | SF | 40 | 52 | 68 | Grouted, reinforced security partitions | 40
04 23 00 | Architectural Masonry Veneer — Office / Entry | SF | 30 | 40 | 55 | Brick/stone veneer at administrative areas | 30
04 01 00 | Masonry Cleaning, Sealing & Restoration | LS | 70000 | 95000 | 130000 | Final cleaning and water-repellent sealing | 70000
06 10 00 | Rough Carpentry — Blocking, Nailers & Curbs | SF | 2.5 | 4 | 6 | Roof blocking, equipment curbs, nailers; per SF GBA | 2.5
06 16 00 | Sheathing — Roof / Wall | SF | 3 | 4.5 | 7 | Gypsum/wood sheathing behind panels; per SF | 3
06 64 00 | FRP Wall Liner Panels — Wet / Service Areas | SF | 6 | 9 | 14 | Fiberglass-reinforced panels at washdown/service | 6
06 83 00 | Fiberglass Grating — Equipment Platforms / Trenches | SF | 22 | 30 | 42 | FRP grating at mechanical platforms and trenches | 22
06 10 10 | Plywood Backboards — Telecom / Electrical | EA | 180 | 260 | 360 | Fire-treated backboards at IDF/electrical rooms | 180
11 13 00 | Loading Dock Equipment — Levelers, Seals, Bumpers | EA | 14000 | 19000 | 26000 | Per dock position; hydraulic levelers, seals, bumpers | 14000
11 13 10 | Dock Lifts / Scissor Lifts — Equipment Handling | EA | 28000 | 38000 | 52000 | Heavy equipment receiving/handling | 28000
11 30 00 | Residential / Pantry Appliances — Break Rooms | LS | 60000 | 85000 | 120000 | Refrigeration, microwaves, dishwashers | 60000
11 40 00 | Foodservice Equipment — Staff Café | LS | 180000 | 260000 | 360000 | Commercial kitchen / servery equipment | 180000
11 24 00 | Facility Maintenance Equipment — Window Washing / Davits | LS | 120000 | 170000 | 240000 | Roof davits and fall-arrest tie-offs | 120000
11 53 00 | Battery / Laboratory Test Equipment | LS | 90000 | 130000 | 180000 | Battery monitoring/test bench equipment | 90000
11 82 00 | Solid Waste Handling — Compactors & Balers | EA | 30000 | 42000 | 58000 | Site compactors and cardboard balers | 30000
12 21 00 | Window Treatments — Blinds / Shades | SF | 8 | 12 | 18 | Manual/motorized shades at office glazing | 8
12 24 00 | Entrance Mats & Grilles | SF | 18 | 26 | 38 | Recessed entrance matting at lobbies | 18
12 35 00 | Specialty Casework — Break / Copy / Support | LF | 280 | 380 | 520 | Plastic-laminate casework; per LF | 280
12 48 00 | Operations Console Systems — NOC / SOC | EA | 6500 | 9000 | 13000 | Per operator position; technical furniture | 6500
12 52 00 | Institutional Furniture — Office / Conference | LS | 220000 | 320000 | 450000 | Systems furniture, conference, lobby | 220000
12 93 00 | Site Furnishings — Benches, Bike Racks, Receptacles | LS | 40000 | 60000 | 85000 | Exterior site amenities | 40000
14 21 00 | Passenger Elevators — Traction (Office Core) | EA | 140000 | 190000 | 260000 | ~2 per building; machine-room-less traction | 140000
14 21 10 | Freight Elevators — Heavy Equipment (12,000 lb) | EA | 320000 | 420000 | 560000 | Equipment-rated freight; ~2 per building | 320000
14 24 00 | Hydraulic Elevators — Service / Low-Rise | EA | 95000 | 130000 | 175000 | Service elevators at support cores | 95000
14 42 00 | Material Lifts / Vertical Reciprocating Conveyors | EA | 45000 | 62000 | 85000 | VRCs for inter-floor equipment moves | 45000
14 91 00 | Hoists & Monorail Cranes — Equipment Rigging | EA | 70000 | 100000 | 140000 | Monorail/jib cranes at mechanical yards | 70000
14 92 00 | Facility Conveying — Tube / Material Transport | LS | 80000 | 120000 | 170000 | Pneumatic tube / small-parts transport | 80000
25 05 00 | Integrated Automation Common Work — OT Cabling & Pathways | SF | 0.8 | 1.2 | 1.8 | Dedicated OT conduit/cable; per SF GBA | 0.8
25 10 00 | Integrated Automation Network — OT Backbone (Switches, Fiber, Segmentation) | LS | 1500000 | 2100000 | 2900000 | Segmented OT/controls network backbone | 1500000
25 11 00 | Integration Servers, Historian & Operator Workstations | EA | 32000 | 45000 | 62000 | Front-end servers, historian, HMI workstations | 32000
25 13 00 | Integration Control Panels — Tie-In / Aggregation (IACP) | EA | 12000 | 17000 | 24000 | Aggregation/tie-in panels (excl. field BMS panels in Div 23) | 12000
25 14 00 | Protocol Gateways / Routers (BACnet / Modbus / SNMP) | EA | 8000 | 12000 | 17000 | Multi-protocol integration gateways | 8000
25 30 00 | Master Systems Integrator (MSI) — Engineering & Point Mapping | MW | 35000 | 50000 | 68000 | MSI engineering, point mapping; per MW IT load | 35000
25 50 00 | Facility Controls Integration — BMS / EPMS / DCIM | LS | 2000000 | 2800000 | 3800000 | Cross-system integration layer; field devices in Div 23/26/27 | 2000000
25 55 00 | Fire Alarm / Security Integration to Automation | LS | 550000 | 780000 | 1100000 | Tie-in of life-safety/security to head-end | 550000
25 90 00 | Sequence of Operations Development & Controls Programming | MW | 22000 | 32000 | 45000 | SOO authoring and programming; per MW | 22000
25 95 00 | Integration Testing, Tuning & Cx Support | LS | 800000 | 1150000 | 1600000 | Integrated systems testing support to Cx | 800000
31 23 20 | Dewatering — Construction | LS | 350000 | 550000 | 850000 | Added detail — earthwork supplemental | 350000
31 05 13 | Aggregate Base Course — Under Slab/Paving | CY | 38 | 52 | 72 | Added detail — earthwork supplemental | 38
31 32 00 | Geotextile / Soil Stabilization Fabric | SF | 0.6 | 0.95 | 1.5 | Added detail — earthwork supplemental | 0.6
32 32 50 | Retaining Walls — Site | SF | 45 | 68 | 98 | Added detail — exterior supplemental | 45
32 17 50 | Guard Rails & Crash Barriers — Site | LF | 55 | 85 | 130 | Added detail — exterior supplemental | 55
33 52 50 | Natural Gas Service & Distribution | LF | 85 | 130 | 195 | Added detail — utilities supplemental | 85
33 82 50 | Communications Ductbank — Site | LF | 140 | 200 | 300 | Added detail — utilities supplemental | 140
03 15 00 | Under-Slab Vapor Barrier & Joints | SF | 1.1 | 1.7 | 2.6 | Added detail — concrete supplemental | 1.1
03 30 70 | Concrete Testing & Inspection | LS | 180000 | 280000 | 420000 | Added detail — concrete supplemental | 180000
05 12 50 | Anchor Bolts & Embed Plates — Structural | LS | 220000 | 340000 | 520000 | Added detail — metals supplemental | 220000
07 27 00 | Air & Vapor Barrier — Building Envelope | SF | 2.2 | 3.4 | 5 | Added detail — thermal/moisture supplemental | 2.2
07 95 00 | Expansion Joint Cover Assemblies | LF | 65 | 95 | 145 | Added detail — thermal/moisture supplemental | 65
22 14 50 | Storm / Sump Pump Systems | EA | 9500 | 14000 | 21000 | Added detail — plumbing supplemental | 9500
08 90 00 | Louvers & Mechanical Vents | SF | 38 | 55 | 82 | Added detail — openings supplemental | 38
09 30 00 | Tiling — Restrooms / Wet Areas | SF | 12 | 18 | 26 | Added detail — finishes supplemental | 12
10 21 50 | Lockers & Locker Room Benches | EA | 280 | 420 | 620 | Added detail — specialties supplemental | 280
27 51 00 | Distributed Antenna System (DAS) — Cellular | LS | 850000 | 1300000 | 1950000 | Added detail — comms supplemental | 850000
27 52 00 | Public Address / Intercom | LS | 280000 | 420000 | 620000 | Added detail — comms supplemental | 280000
11 13 50 | Loading Dock Shelters / Canopies | EA | 12000 | 18000 | 27000 | Added detail — equipment supplemental | 12000
31 23 30 | Rock Excavation & Blasting | CY | 65 | 95 | 140 | Added detail — client estimate granularity | 65
31 23 40 | Surplus Soil Export & Haul-Off | CY | 14 | 22 | 34 | Added detail — client estimate granularity | 14
31 11 50 | Temporary Construction Roads & Laydown | LS | 600000 | 950000 | 1450000 | Added detail — client estimate granularity | 600000
32 13 50 | Heavy-Duty Concrete Hardstand — Equipment Yard | SF | 14 | 20 | 28 | Added detail — client estimate granularity | 14
32 12 50 | Truck Court & Dock Apron Paving | SF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
33 12 50 | Domestic Water Booster Pump Station | EA | 180000 | 280000 | 420000 | Added detail — client estimate granularity | 180000
33 31 50 | Sanitary Lift Station | LS | 350000 | 550000 | 850000 | Added detail — client estimate granularity | 350000
33 09 50 | Utility SCADA / Monitoring | LS | 280000 | 440000 | 680000 | Added detail — client estimate granularity | 280000
03 30 80 | Cast-in-Place — Mat Foundation / Raft | CY | 320 | 430 | 600 | Added detail — client estimate granularity | 320
03 30 95 | Cast-in-Place — Pile Caps & Grade Beams | CY | 380 | 520 | 720 | Added detail — client estimate granularity | 380
03 35 50 | Concrete Floor Hardener & Sealer | SF | 1.4 | 2.2 | 3.4 | Added detail — client estimate granularity | 1.4
05 31 50 | Equipment / Roof Screen Framing | LB | 4.5 | 6.5 | 9.5 | Added detail — client estimate granularity | 4.5
05 51 50 | Catwalks & Crossover Platforms | SF | 95 | 140 | 210 | Added detail — client estimate granularity | 95
07 18 00 | Traffic Coating — Ramps / Parking Deck | SF | 7 | 10 | 15 | Added detail — client estimate granularity | 7
07 72 50 | Roof Walkway / Equipment Ballast Pavers | SF | 12 | 18 | 27 | Added detail — client estimate granularity | 12
22 31 50 | Reverse Osmosis / DI Water System | LS | 1200000 | 1850000 | 2750000 | Added detail — client estimate granularity | 1200000
22 14 60 | Trench Drains — Mechanical / Generator Rooms | LF | 95 | 140 | 210 | Added detail — client estimate granularity | 95
22 67 00 | Process Water Piping — Liquid Cooling Makeup | LF | 110 | 165 | 250 | Added detail — client estimate granularity | 110
21 16 00 | Foam Suppression — Fuel Storage / Generator | LS | 650000 | 980000 | 1450000 | Added detail — client estimate granularity | 650000
21 11 50 | Fire Water Yard Loop & Hydrants | LF | 110 | 160 | 240 | Added detail — client estimate granularity | 110
23 09 50 | Variable Frequency Drives — Mechanical | EA | 18000 | 27000 | 40000 | Added detail — client estimate granularity | 18000
23 34 50 | Generator Room / Equipment Ventilation Fans | EA | 22000 | 33000 | 49000 | Added detail — client estimate granularity | 22000
23 25 50 | Glycol Feed & Chemical Treatment | LS | 480000 | 740000 | 1100000 | Added detail — client estimate granularity | 480000
26 27 50 | Motor Control Centers — Mechanical | EA | 85000 | 125000 | 185000 | Added detail — client estimate granularity | 85000
26 05 60 | Feeder Cable & Terminations — LV | LF | 85 | 125 | 185 | Added detail — client estimate granularity | 85
26 32 50 | Battery Energy Storage (BESS) Tie-In | LS | 2800000 | 4200000 | 6300000 | Added detail — client estimate granularity | 2800000
08 31 50 | Fire-Rated Door Assemblies — Rated Corridors | EA | 2400 | 3500 | 5200 | Added detail — client estimate granularity | 2400
08 62 00 | Skylights / Glazed Smoke Vents | EA | 6500 | 9800 | 14500 | Added detail — client estimate granularity | 6500
09 77 00 | Acoustic Wall Panels — NOC / Conference | SF | 14 | 21 | 31 | Added detail — client estimate granularity | 14
09 67 50 | Resinous Flooring — Mechanical / Pump Rooms | SF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
10 26 50 | Wall & Door Protection — Impact Rails | LF | 28 | 42 | 62 | Added detail — client estimate granularity | 28
10 73 01 | Exterior Canopies & Walkway Covers | SF | 65 | 95 | 140 | Added detail — client estimate granularity | 65
27 05 60 | Telecom Bonding & Grounding (TBB/TGB) | LS | 280000 | 430000 | 650000 | Added detail — client estimate granularity | 280000
27 53 00 | Two-Way Radio / BDA Coverage System | LS | 650000 | 980000 | 1450000 | Added detail — client estimate granularity | 650000
28 13 50 | Optical Turnstiles — Lobby | EA | 28000 | 42000 | 62000 | Added detail — client estimate granularity | 28000
28 16 50 | Duress / Panic Alarm System | LS | 280000 | 430000 | 650000 | Added detail — client estimate granularity | 280000
04 73 00 | Manufactured Stone Veneer — Entry | SF | 38 | 55 | 82 | Added detail — client estimate granularity | 38
06 41 00 | Architectural Millwork — Lobby / Reception | LS | 350000 | 550000 | 850000 | Added detail — client estimate granularity | 350000
11 12 00 | Parking Control Equipment — Gates / Ticketing | LS | 220000 | 340000 | 520000 | Added detail — client estimate granularity | 220000
11 13 60 | Vehicle Scale — Truck Weighing | EA | 95000 | 145000 | 220000 | Added detail — client estimate granularity | 95000
31 22 50 | Topsoil Stripping & Stockpiling | CY | 8 | 12 | 18 | Added detail — client estimate granularity | 8
31 22 60 | Fine Grading & Subgrade Preparation | SF | 0.4 | 0.65 | 1 | Added detail — client estimate granularity | 0.4
32 17 60 | Parking Bumpers & Wheel Stops | EA | 65 | 95 | 140 | Added detail — client estimate granularity | 65
32 84 50 | Site Stormwater — Inlets, Manholes & Catch Basins | EA | 3200 | 4800 | 7200 | Added detail — client estimate granularity | 3200
33 05 50 | Utility Trenching, Bedding & Backfill | LF | 28 | 42 | 62 | Added detail — client estimate granularity | 28
03 15 50 | Waterstops & Construction Joints | LF | 18 | 27 | 40 | Added detail — client estimate granularity | 18
03 62 50 | Non-Shrink Grout — Equipment Base Plates | CF | 45 | 68 | 100 | Added detail — client estimate granularity | 45
05 50 60 | Loose Lintels & Misc Embedded Steel | LB | 4 | 6 | 9 | Added detail — client estimate granularity | 4
05 53 50 | Metal Bar Grating — Trenches / Pits | SF | 38 | 55 | 82 | Added detail — client estimate granularity | 38
7 71 01 | Gutters, Downspouts & Scuppers | LF | 28 | 42 | 62 | Added detail — client estimate granularity | 28
07 13 50 | Below-Grade Waterproofing — Pits / Vaults | SF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
22 13 60 | Floor Drains, Roof Drains & Cleanouts | EA | 650 | 980 | 1450 | Added detail — client estimate granularity | 650
22 07 50 | Plumbing Piping Insulation | LF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
21 12 50 | Jockey Pump & Fire Pump Test Header | LS | 180000 | 280000 | 420000 | Added detail — client estimate granularity | 180000
21 11 60 | Fire Department Connections & Hydrant Valves | EA | 3500 | 5200 | 7800 | Added detail — client estimate granularity | 3500
23 33 00 | Air Terminal Units — VAV / Fan-Powered Boxes | EA | 1800 | 2700 | 4000 | Added detail — client estimate granularity | 1800
23 37 50 | Diffusers, Registers & Grilles | EA | 220 | 330 | 490 | Added detail — client estimate granularity | 220
23 33 50 | Fire / Smoke Dampers | EA | 850 | 1300 | 1950 | Added detail — client estimate granularity | 850
23 21 60 | CHW/HW Valves, Expansion Tanks & Air Separators | LS | 850000 | 1300000 | 1950000 | Added detail — client estimate granularity | 850000
26 05 36 | Cable Tray & Wireway Systems — Electrical | LF | 65 | 95 | 140 | Added detail — client estimate granularity | 65
26 27 60 | Wiring Devices & Receptacles | EA | 95 | 140 | 210 | Added detail — client estimate granularity | 95
08 71 60 | Automatic Door Operators — ADA / Vestibule | EA | 6500 | 9800 | 14500 | Added detail — client estimate granularity | 6500
8 14 01 | Wood Doors — Office / Administrative | EA | 850 | 1300 | 1950 | Added detail — client estimate granularity | 850
09 22 50 | Gypsum Ceilings & Soffits — Hard-Lid | SF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
09 65 50 | Resilient Base & Accessories | LF | 6 | 9 | 14 | Added detail — client estimate granularity | 6
10 11 50 | Visual Display Boards — Markerboards / Tackboards | EA | 480 | 720 | 1080 | Added detail — client estimate granularity | 480
10 22 50 | Operable / Demountable Partitions — Conference | SF | 65 | 95 | 140 | Added detail — client estimate granularity | 65
27 32 50 | Master Clock / Timing Distribution | LS | 220000 | 340000 | 520000 | Added detail — client estimate granularity | 220000
27 21 50 | KVM / Console Management — Data Halls | LS | 480000 | 740000 | 1100000 | Added detail — client estimate granularity | 480000
28 13 60 | Weapons / Package Screening — Lobby | LS | 280000 | 430000 | 650000 | Added detail — client estimate granularity | 280000
28 16 60 | Rising Bollards — Vehicle Sally Port | EA | 45000 | 68000 | 100000 | Added detail — client estimate granularity | 45000
04 21 50 | Brick Veneer — Office Facade | SF | 32 | 48 | 72 | Added detail — client estimate granularity | 32
6 64 01 | Solid Surface Fabrications — Reception / Break | LS | 180000 | 280000 | 420000 | Added detail — client estimate granularity | 180000
12 36 00 | Countertops — Break / Pantry / Casework | LS | 220000 | 340000 | 520000 | Added detail — client estimate granularity | 220000
31 25 50 | SWPPP & Construction Fence | LS | 180000 | 280000 | 420000 | Added detail — client estimate granularity | 180000
03 11 50 | Concrete Formwork — Walls & Columns | SF | 9 | 13 | 19 | Added detail — client estimate granularity | 9
22 33 50 | Domestic Water Heaters & Recirculation | EA | 12000 | 18000 | 27000 | Added detail — client estimate granularity | 12000
22 11 50 | Hose Bibbs & Wall Hydrants | EA | 450 | 680 | 1000 | Added detail — client estimate granularity | 450
21 13 70 | Sprinkler Piping, Heads & Risers — Office/Support | SF | 4 | 6 | 9 | Added detail — client estimate granularity | 4
23 31 50 | Ductwork — Galvanized Supply / Return / Exhaust | LB | 9 | 13 | 19 | Added detail — client estimate granularity | 9
23 07 50 | Duct & Pipe Insulation — Mechanical | SF | 4 | 6 | 9 | Added detail — client estimate granularity | 4
23 05 50 | Mechanical Seismic Restraints & Hangers | LS | 650000 | 980000 | 1450000 | Added detail — client estimate granularity | 650000
23 05 93 | Testing, Adjusting & Balancing (TAB) | LS | 480000 | 740000 | 1100000 | Added detail — client estimate granularity | 480000
26 05 26 | Grounding & Bonding — Electrical Ground Grid | LS | 850000 | 1300000 | 1950000 | Added detail — client estimate granularity | 850000
26 41 01 | Lightning Protection System | LS | 350000 | 550000 | 850000 | Added detail — client estimate granularity | 350000
26 05 73 | Arc-Flash & Coordination Study | LS | 180000 | 280000 | 420000 | Added detail — client estimate granularity | 180000
26 51 50 | Emergency & Egress Lighting | EA | 280 | 420 | 620 | Added detail — client estimate granularity | 280
8 36 01 | Sectional Overhead Doors — Loading / Service | EA | 6500 | 9800 | 14500 | Added detail — client estimate granularity | 6500
8 71 01 | Door Hardware Sets — Finish Hardware | EA | 850 | 1300 | 1950 | Added detail — client estimate granularity | 850
9 68 01 | Carpet & Resilient Flooring — Office Areas | SF | 6 | 9 | 13 | Added detail — client estimate granularity | 6
09 91 50 | Intumescent Coatings — Exposed Structural Steel | SF | 4 | 6 | 9 | Added detail — client estimate granularity | 4
10 28 01 | Toilet & Bath Accessories | EA | 220 | 330 | 490 | Added detail — client estimate granularity | 220
10 21 13 | Toilet Partitions — Phenolic | EA | 850 | 1300 | 1950 | Added detail — client estimate granularity | 850
27 05 28 | Telecom Pathways — Innerduct & Sleeves | LF | 12 | 18 | 27 | Added detail — client estimate granularity | 12
23 23 11 | In-Row Cooling — Units (Equipment) | LS | 63525000 | 90750000 | 127050000 | Decomposed from 23 23 10 | 63525000
23 23 12 | In-Row Cooling — Refrigerant / CW Piping | LS | 20790000 | 29700000 | 41580000 | Decomposed from 23 23 10 | 20790000
23 23 13 | In-Row Cooling — Controls & Integration | LS | 13860000 | 19800000 | 27720000 | Decomposed from 23 23 10 | 13860000
23 23 14 | In-Row Cooling — Rigging, Install & Seismic | LS | 11550000 | 16500000 | 23100000 | Decomposed from 23 23 10 | 11550000
23 23 15 | In-Row Cooling — Startup & Commissioning | LS | 5775000 | 8250000 | 11550000 | Decomposed from 23 23 10 | 5775000
26 32 01 | PDU — Units | LS | 15624000 | 29016000 | 49104000 | Decomposed from 26 32 00 | 15624000
26 32 02 | PDU — Output Distribution Panels & Breakers | LS | 4536000 | 8424000 | 14256000 | Decomposed from 26 32 00 | 4536000
26 32 03 | PDU — Monitoring & Metering | LS | 2520000 | 4680000 | 7920000 | Decomposed from 26 32 00 | 2520000
26 32 04 | PDU — Install & Terminations | LS | 2520000 | 4680000 | 7920000 | Decomposed from 26 32 00 | 2520000
23 70 01 | TES — Storage Tanks | LS | 12600000 | 18000000 | 25200000 | Decomposed from 23 70 00 | 12600000
23 70 02 | TES — Glycol Charge & Water Treatment | LS | 3780000 | 5400000 | 7560000 | Decomposed from 23 70 00 | 3780000
23 70 03 | TES — Pumps & Piping | LS | 5040000 | 7200000 | 10080000 | Decomposed from 23 70 00 | 5040000
23 70 04 | TES — Controls & Insulation | LS | 2520000 | 3600000 | 5040000 | Decomposed from 23 70 00 | 2520000
23 70 05 | TES — Commissioning | LS | 1260000 | 1800000 | 2520000 | Decomposed from 23 70 00 | 1260000
26 20 01 | Generators — Diesel Gensets | LS | 13500000 | 23625000 | 37125000 | Decomposed from 26 20 00 | 13500000
26 20 02 | Generators — Fuel Day Tanks, Exhaust & Silencers | LS | 3375000 | 5906250 | 9281250 | Decomposed from 26 20 00 | 3375000
26 20 03 | Generators — Paralleling Switchgear & Controls | LS | 3375000 | 5906250 | 9281250 | Decomposed from 26 20 00 | 3375000
26 20 04 | Generators — Install, Rigging & Commissioning | LS | 2250000 | 3937500 | 6187500 | Decomposed from 26 20 00 | 2250000
26 30 01 | UPS — Modules | LS | 12375000 | 22275000 | 34650000 | Decomposed from 26 30 00 | 12375000
26 30 02 | UPS — Battery Systems | LS | 5625000 | 10125000 | 15750000 | Decomposed from 26 30 00 | 5625000
26 30 03 | UPS — Input/Output Switchgear | LS | 2700000 | 4860000 | 7560000 | Decomposed from 26 30 00 | 2700000
26 30 04 | UPS — Install & Commissioning | LS | 1800000 | 3240000 | 5040000 | Decomposed from 26 30 00 | 1800000
23 21 01 | Chillers — Units | LS | 12722400 | 19083600 | 28625400 | Decomposed from 23 21 00 | 12722400
23 21 02 | Chillers — Refrigerant Charge & VFDs | LS | 2462400 | 3693600 | 5540400 | Decomposed from 23 21 00 | 2462400
23 21 03 | Chillers — Rigging & Install | LS | 3283200 | 4924800 | 7387200 | Decomposed from 23 21 00 | 3283200
23 21 04 | Chillers — Startup & Commissioning | LS | 2052000 | 3078000 | 4617000 | Decomposed from 23 21 00 | 2052000
33 71 01 | Utility Substation & Transformers | LS | 10125000 | 18225000 | 30375000 | Decomposed from 33 71 00 | 10125000
33 71 02 | Primary Feeders & Duct Bank | LS | 5625000 | 10125000 | 16875000 | Decomposed from 33 71 00 | 5625000
33 71 03 | Metering & Protection Relays | LS | 3375000 | 6075000 | 10125000 | Decomposed from 33 71 00 | 3375000
33 71 04 | Utility Coordination & Switchgear | LS | 3375000 | 6075000 | 10125000 | Decomposed from 33 71 00 | 3375000
26 33 01 | Busway — Runs | LS | 8580000 | 15730000 | 25740000 | Decomposed from 26 33 00 | 8580000
26 33 02 | Busway — Supports & Hangers | LS | 1980000 | 3630000 | 5940000 | Decomposed from 26 33 00 | 1980000
26 33 03 | Busway — Connections & Terminations | LS | 2640000 | 4840000 | 7920000 | Decomposed from 26 33 00 | 2640000
27 20 01 | Fiber — Panels & Enclosures | LS | 6930000 | 9900000 | 13860000 | Decomposed from 27 20 00 | 6930000
27 20 02 | Fiber — Cassettes / Modules | LS | 4158000 | 5940000 | 8316000 | Decomposed from 27 20 00 | 4158000
27 20 03 | Fiber — Terminations & Testing | LS | 2772000 | 3960000 | 5544000 | Decomposed from 27 20 00 | 2772000
33 50 11 | Fuel — Day Tanks & Bulk Piping | LS | 5315625 | 7593750 | 10631250 | Decomposed from 33 50 10 | 5315625
33 50 12 | Fuel — Pumps, Filtration & Polishing | LS | 2953125 | 4218750 | 5906250 | Decomposed from 33 50 10 | 2953125
33 50 13 | Fuel — Controls & Leak Detection | LS | 1771875 | 2531250 | 3543750 | Decomposed from 33 50 10 | 1771875
33 50 14 | Fuel — Install & Testing | LS | 1771875 | 2531250 | 3543750 | Decomposed from 33 50 10 | 1771875
5 12 01 | Steel — Fabricated (Columns/Beams) | LS | 6720000 | 9600000 | 14400000 | Decomposed from 05 12 00 | 6720000
5 12 02 | Steel — Erection & Connections | LS | 2800000 | 4000000 | 6000000 | Decomposed from 05 12 00 | 2800000
5 12 03 | Steel — Shop Priming & Coatings | LS | 896000 | 1280000 | 1920000 | Decomposed from 05 12 00 | 896000
5 12 04 | Steel — Detailing & Engineering | LS | 784000 | 1120000 | 1680000 | Decomposed from 05 12 00 | 784000
27 15 01 | IT Racks — Cabinets / Racks | LS | 7150000 | 14300000 | 24310000 | Decomposed from 27 15 00 | 7150000
27 15 02 | IT Racks — Rack PDUs / Power Strips | LS | 2200000 | 4400000 | 7480000 | Decomposed from 27 15 00 | 2200000
27 15 03 | IT Racks — Containment & Accessories | LS | 1650000 | 3300000 | 5610000 | Decomposed from 27 15 00 | 1650000
22 15 01 | Makeup Water — Storage Tanks | LS | 4104000 | 7695000 | 12825000 | Decomposed from 22 15 00 | 4104000
22 15 02 | Makeup Water — Treatment & Filtration | LS | 3078000 | 5771250 | 9618750 | Decomposed from 22 15 00 | 3078000
22 15 03 | Makeup Water — Pumps & Piping | LS | 2052000 | 3847500 | 6412500 | Decomposed from 22 15 00 | 2052000
22 15 04 | Makeup Water — Controls | LS | 1026000 | 1923750 | 3206250 | Decomposed from 22 15 00 | 1026000
9 69 01 | Raised Floor — Panels & Pedestals | LS | 6776000 | 10780000 | 16940000 | Decomposed from 09 69 00 | 6776000
9 69 02 | Raised Floor — Ramps, Stairs & Transitions | LS | 1161600 | 1848000 | 2904000 | Decomposed from 09 69 00 | 1161600
9 69 03 | Raised Floor — Cutouts, Grommets & Accessories | LS | 968000 | 1540000 | 2420000 | Decomposed from 09 69 00 | 968000
9 69 04 | Raised Floor — Leveling & Install | LS | 774400 | 1232000 | 1936000 | Decomposed from 09 69 00 | 774400
26 30 12 | UPS Batteries — Cells / Strings | LS | 6300000 | 11025000 | 17325000 | Decomposed from 26 30 10 | 6300000
26 30 13 | UPS Batteries — Racks / Cabinets | LS | 1350000 | 2362500 | 3712500 | Decomposed from 26 30 10 | 1350000
26 30 14 | UPS Batteries — Monitoring (BMS) | LS | 900000 | 1575000 | 2475000 | Decomposed from 26 30 10 | 900000
26 30 15 | UPS Batteries — Install | LS | 450000 | 787500 | 1237500 | Decomposed from 26 30 10 | 450000
26 31 01 | STS — Units | LS | 6300000 | 12600000 | 21420000 | Decomposed from 26 31 00 | 6300000
26 31 02 | STS — Enclosures & Bypass | LS | 1620000 | 3240000 | 5508000 | Decomposed from 26 31 00 | 1620000
26 31 03 | STS — Install & Terminations | LS | 1080000 | 2160000 | 3672000 | Decomposed from 26 31 00 | 1080000
26 32 11 | RPP — Panels | LS | 5733000 | 8190000 | 11466000 | Decomposed from 26 32 10 | 5733000
26 32 12 | RPP — Branch Breakers | LS | 1764000 | 2520000 | 3528000 | Decomposed from 26 32 10 | 1764000
26 32 13 | RPP — Monitoring & Install | LS | 1323000 | 1890000 | 2646000 | Decomposed from 26 32 10 | 1323000
26 33 11 | Tap-Off Boxes — Units | LS | 6174000 | 8820000 | 12348000 | Decomposed from 26 33 10 | 6174000
26 33 12 | Tap-Off Boxes — Breakers | LS | 1587600 | 2268000 | 3175200 | Decomposed from 26 33 10 | 1587600
26 33 13 | Tap-Off Boxes — Install | LS | 1058400 | 1512000 | 2116800 | Decomposed from 26 33 10 | 1058400
3 40 01 | Tilt-Up — Panel Fabrication | LS | 5184000 | 8064000 | 12096000 | Decomposed from 03 40 00 | 5184000
3 40 02 | Tilt-Up — Erection & Bracing | LS | 2160000 | 3360000 | 5040000 | Decomposed from 03 40 00 | 2160000
3 40 03 | Tilt-Up — Connections & Joints | LS | 864000 | 1344000 | 2016000 | Decomposed from 03 40 00 | 864000
3 40 04 | Tilt-Up — Finishing | LS | 432000 | 672000 | 1008000 | Decomposed from 03 40 00 | 432000
7 41 01 | Wall Panels — Panels & Insulation | LS | 5616000 | 8736000 | 13104000 | Decomposed from 07 41 00 | 5616000
7 41 02 | Wall Panels — Subgirts & Attachment | LS | 1728000 | 2688000 | 4032000 | Decomposed from 07 41 00 | 1728000
7 41 03 | Wall Panels — Flashing & Trim | LS | 1296000 | 2016000 | 3024000 | Decomposed from 07 41 00 | 1296000
31 62 01 | Driven Piles — Pile Material | LS | 4200000 | 6600000 | 10200000 | Decomposed from 31 62 00 | 4200000
31 62 02 | Driven Piles — Driving & Equipment | LS | 2940000 | 4620000 | 7140000 | Decomposed from 31 62 00 | 2940000
31 62 03 | Driven Piles — Testing & PDA | LS | 840000 | 1320000 | 2040000 | Decomposed from 31 62 00 | 840000
31 62 04 | Driven Piles — Cutoffs & Prep | LS | 420000 | 660000 | 1020000 | Decomposed from 31 62 00 | 420000
26 20 11 | Paralleling Switchgear — Gear | LS | 4882500 | 6975000 | 9765000 | Decomposed from 26 20 10 | 4882500
26 20 12 | Paralleling Switchgear — Controls & Sync | LS | 1575000 | 2250000 | 3150000 | Decomposed from 26 20 10 | 1575000
26 20 13 | Paralleling Switchgear — Install & Commissioning | LS | 1417500 | 2025000 | 2835000 | Decomposed from 26 20 10 | 1417500
33 52 01 | Fuel Piping — Piping & Fittings | LS | 4331250 | 6187500 | 8662500 | Decomposed from 33 52 00 | 4331250
33 52 02 | Fuel Piping — Fill Station & Pumps | LS | 1968750 | 2812500 | 3937500 | Decomposed from 33 52 00 | 1968750
33 52 03 | Fuel Piping — Supports & Insulation | LS | 945000 | 1350000 | 1890000 | Decomposed from 33 52 00 | 945000
33 52 04 | Fuel Piping — Testing | LS | 630000 | 900000 | 1260000 | Decomposed from 33 52 00 | 630000
7 81 01 | Fireproofing — Material & Application | LS | 5880000 | 8400000 | 11760000 | Decomposed from 07 81 00 | 5880000
7 81 02 | Fireproofing — Prep & Masking | LS | 1176000 | 1680000 | 2352000 | Decomposed from 07 81 00 | 1176000
7 81 03 | Fireproofing — Patching & Touch-Up | LS | 784000 | 1120000 | 1568000 | Decomposed from 07 81 00 | 784000
26 12 01 | Switchboards — Units | LS | 4998000 | 7140000 | 9996000 | Decomposed from 26 12 00 | 4998000
26 12 02 | Switchboards — Breakers & Metering | LS | 1470000 | 2100000 | 2940000 | Decomposed from 26 12 00 | 1470000
26 12 03 | Switchboards — Install & Terminations | LS | 882000 | 1260000 | 1764000 | Decomposed from 26 12 00 | 882000
26 14 01 | Panelboards (Mech) — Boards | LS | 3906000 | 5580000 | 7812000 | Decomposed from 26 14 00 | 3906000
26 14 02 | Panelboards (Mech) — Breakers | LS | 1386000 | 1980000 | 2772000 | Decomposed from 26 14 00 | 1386000
26 14 03 | Panelboards (Mech) — Install | LS | 1008000 | 1440000 | 2016000 | Decomposed from 26 14 00 | 1008000
23 23 01 | CRAH — Units | LS | 3816720 | 6043140 | 8905680 | Decomposed from 23 23 00 | 3816720
23 23 02 | CRAH — Piping & Coils | LS | 1108080 | 1754460 | 2585520 | Decomposed from 23 23 00 | 1108080
23 23 03 | CRAH — Controls | LS | 738720 | 1169640 | 1723680 | Decomposed from 23 23 00 | 738720
23 23 04 | CRAH — Install | LS | 492480 | 779760 | 1149120 | Decomposed from 23 23 00 | 492480
5 52 01 | Seismic Supports — Steel & Bracing | LS | 3780000 | 5400000 | 7560000 | Decomposed from 05 52 00 | 3780000
5 52 02 | Seismic Supports — Snubbers & Isolators | LS | 1575000 | 2250000 | 3150000 | Decomposed from 05 52 00 | 1575000
5 52 03 | Seismic Supports — Anchorage & Install | LS | 945000 | 1350000 | 1890000 | Decomposed from 05 52 00 | 945000
26 14 11 | Panelboards (Lighting) — Boards | LS | 3628800 | 5184000 | 7257600 | Decomposed from 26 14 10 | 3628800
26 14 12 | Panelboards (Lighting) — Breakers | LS | 1330560 | 1900800 | 2661120 | Decomposed from 26 14 10 | 1330560
26 14 13 | Panelboards (Lighting) — Install | LS | 1088640 | 1555200 | 2177280 | Decomposed from 26 14 10 | 1088640
7 52 01 | TPO Roofing — Membrane & Insulation | LS | 3968000 | 6448000 | 9920000 | Decomposed from 07 52 00 | 3968000
7 52 02 | TPO Roofing — Fasteners & Adhesive | LS | 1152000 | 1872000 | 2880000 | Decomposed from 07 52 00 | 1152000
7 52 03 | TPO Roofing — Flashing & Details | LS | 1280000 | 2080000 | 3200000 | Decomposed from 07 52 00 | 1280000
28 10 11 | Mantrap — Interlock Doors & Controllers | LS | 2800000 | 5200000 | 8800000 | Decomposed from 28 10 10 | 2800000
28 10 12 | Mantrap — Readers & Biometrics | LS | 1400000 | 2600000 | 4400000 | Decomposed from 28 10 10 | 1400000
28 10 13 | Mantrap — Integration & Software | LS | 840000 | 1560000 | 2640000 | Decomposed from 28 10 10 | 840000
28 10 14 | Mantrap — Install | LS | 560000 | 1040000 | 1760000 | Decomposed from 28 10 10 | 560000
9 21 01 | Gypsum — Framing & Studs | LS | 2304000 | 3840000 | 6144000 | Decomposed from 09 21 00 | 2304000
9 21 02 | Gypsum — Board & Install | LS | 2304000 | 3840000 | 6144000 | Decomposed from 09 21 00 | 2304000
9 21 03 | Gypsum — Taping & Finishing | LS | 1152000 | 1920000 | 3072000 | Decomposed from 09 21 00 | 1152000
31 63 01 | Drilled Shafts — Drilling | LS | 2800000 | 4000000 | 5600000 | Decomposed from 31 63 00 | 2800000
31 63 02 | Drilled Shafts — Concrete & Rebar | LS | 1680000 | 2400000 | 3360000 | Decomposed from 31 63 00 | 1680000
31 63 03 | Drilled Shafts — Casing | LS | 672000 | 960000 | 1344000 | Decomposed from 31 63 00 | 672000
31 63 04 | Drilled Shafts — Testing | LS | 448000 | 640000 | 896000 | Decomposed from 31 63 00 | 448000
21 22 01 | FM-200 — Agent & Cylinders | LS | 2640000 | 4840000 | 7700000 | Decomposed from 21 22 00 | 2640000
21 22 02 | FM-200 — Piping & Nozzles | LS | 1320000 | 2420000 | 3850000 | Decomposed from 21 22 00 | 1320000
21 22 03 | FM-200 — Detection & Controls | LS | 792000 | 1452000 | 2310000 | Decomposed from 21 22 00 | 792000
21 22 04 | FM-200 — Install | LS | 528000 | 968000 | 1540000 | Decomposed from 21 22 00 | 528000
23 22 01 | Cooling Towers — Towers | LS | 3180600 | 5566050 | 8746650 | Decomposed from 23 22 00 | 3180600
23 22 02 | Cooling Towers — Basins & Fans | LS | 923400 | 1615950 | 2539350 | Decomposed from 23 22 00 | 923400
23 22 03 | Cooling Towers — Install & Rigging | LS | 615600 | 1077300 | 1692900 | Decomposed from 23 22 00 | 615600
23 22 04 | Cooling Towers — Controls | LS | 410400 | 718200 | 1128600 | Decomposed from 23 22 00 | 410400
26 20 41 | Gen Enclosures — Enclosures | LS | 3051562.5 | 4359375 | 6103125 | Decomposed from 26 20 40 | 3051562.5
26 20 42 | Gen Enclosures — Sound Attenuation | LS | 1230468.75 | 1757812.5 | 2460937.5 | Decomposed from 26 20 40 | 1230468.75
26 20 43 | Gen Enclosures — Install | LS | 639843.75 | 914062.5 | 1279687.5 | Decomposed from 26 20 40 | 639843.75
26 05 01 | Common Work — Conduit & Raceway | LS | 2464000 | 3520000 | 4928000 | Decomposed from 26 05 00 | 2464000
26 05 02 | Common Work — Wire & Cable | LS | 1344000 | 1920000 | 2688000 | Decomposed from 26 05 00 | 1344000
26 05 03 | Common Work — Boxes & Fittings | LS | 672000 | 960000 | 1344000 | Decomposed from 26 05 00 | 672000
27 21 01 | Copper Panels — Panels | LS | 2541000 | 3630000 | 5082000 | Decomposed from 27 21 00 | 2541000
27 21 02 | Copper Panels — Jacks & Modules | LS | 1386000 | 1980000 | 2772000 | Decomposed from 27 21 00 | 1386000
27 21 03 | Copper Panels — Terminations & Testing | LS | 693000 | 990000 | 1386000 | Decomposed from 27 21 00 | 693000
26 05 61 | LV Feeder — Cable | LS | 3088296.2518 | 4541612.135 | 6721585.9598 | Decomposed from 26 05 60 | 3088296.2518
26 05 62 | LV Feeder — Terminations | LS | 1286790.1049 | 1892338.3896 | 2800660.8166 | Decomposed from 26 05 60 | 1286790.1049
26 05 63 | LV Feeder — Testing | LS | 772074.063 | 1135403.0337 | 1680396.49 | Decomposed from 26 05 60 | 772074.063
27 15 11 | Cabinet Accessories — Blanking Panels | LS | 1865088.7167 | 2664412.4526 | 3730177.4336 | Decomposed from 27 15 10 | 1865088.7167
27 15 12 | Cabinet Accessories — Cable Management | LS | 1631952.6271 | 2331360.896 | 3263905.2544 | Decomposed from 27 15 10 | 1631952.6271
27 15 13 | Cabinet Accessories — Grounding & Hardware | LS | 1165680.448 | 1665257.7829 | 2331360.896 | Decomposed from 27 15 10 | 1165680.448
23 31 51 | Ductwork — Sheet Metal | LS | 2615968.5898 | 3778621.2963 | 5522600.3562 | Decomposed from 23 31 50 | 2615968.5898
23 31 52 | Ductwork — Fittings & Dampers | LS | 1089986.9124 | 1574425.5401 | 2301083.4817 | Decomposed from 23 31 50 | 1089986.9124
23 31 53 | Ductwork — Hangers & Sealing | LS | 653992.1475 | 944655.324 | 1380650.089 | Decomposed from 23 31 50 | 653992.1475
3 30 31 | Slab on Grade — Concrete | LS | 3330515.5656 | 5328824.9051 | 7993237.3576 | Decomposed from 03 30 30 | 3330515.5656
3 30 32 | Slab on Grade — Reinforcement | LS | 1211096.5694 | 1937754.5109 | 2906631.7664 | Decomposed from 03 30 30 | 1211096.5694
3 30 33 | Slab on Grade — Finishing & Curing | LS | 908322.427 | 1453315.8832 | 2179973.8248 | Decomposed from 03 30 30 | 908322.427
3 30 34 | Slab on Grade — Vapor Barrier Prep | LS | 605548.2846 | 968877.2555 | 1453315.8832 | Decomposed from 03 30 30 | 605548.2846
27 32 01 | Leak Detection — Sensing Cable | LS | 2220343.7105 | 3996618.6788 | 6661031.1314 | Decomposed from 27 32 00 | 2220343.7105
27 32 02 | Leak Detection — Controllers | LS | 1332206.2263 | 2397971.2073 | 3996618.6788 | Decomposed from 27 32 00 | 1332206.2263
27 32 03 | Leak Detection — Integration & Install | LS | 888137.4842 | 1598647.4715 | 2664412.4526 | Decomposed from 27 32 00 | 888137.4842
23 24 01 | Hot Aisle — Panels & Doors | LS | 2664412.4526 | 4995773.3485 | 8326288.9142 | Decomposed from 23 24 00 | 2664412.4526
23 24 02 | Hot Aisle — Roof / Ceiling | LS | 1110171.8552 | 2081572.2286 | 3469287.0476 | Decomposed from 23 24 00 | 1110171.8552
23 24 03 | Hot Aisle — Install | LS | 666103.1131 | 1248943.3372 | 2081572.2286 | Decomposed from 23 24 00 | 666103.1131
5 31 01 | Roof Deck — Decking | LS | 1525981.6773 | 2373749.2759 | 3391070.3941 | Decomposed from 05 31 00 | 1525981.6773
5 31 02 | Roof Deck — Fasteners & Accessories | LS | 326996.0737 | 508660.5591 | 726657.9416 | Decomposed from 05 31 00 | 326996.0737
5 31 03 | Roof Deck — Install | LS | 326996.0737 | 508660.5591 | 726657.9416 | Decomposed from 05 31 00 | 326996.0737
8 44 01 | Curtain Wall — Framing & Glazing | LS | 1377622.3476 | 1968031.9251 | 2755244.6952 | Decomposed from 08 44 00 | 1377622.3476
8 44 02 | Curtain Wall — Install | LS | 423883.7993 | 605548.2846 | 847767.5985 | Decomposed from 08 44 00 | 423883.7993
8 44 03 | Curtain Wall — Sealants & Flashing | LS | 317912.8495 | 454161.2135 | 635825.6989 | Decomposed from 08 44 00 | 317912.8495
23 09 51 | VFDs — Drives | LS | 2288972.516 | 3433458.774 | 5086605.5912 | Decomposed from 23 09 50 | 2288972.516
23 09 52 | VFDs — Enclosures | LS | 490494.1105 | 735741.1659 | 1089986.9124 | Decomposed from 23 09 50 | 490494.1105
23 09 53 | VFDs — Install & Programming | LS | 490494.1105 | 735741.1659 | 1089986.9124 | Decomposed from 23 09 50 | 490494.1105
23 40 01 | Makeup Water Sys — Tanks | LS | 1292760 | 1846800 | 2585520 | Decomposed from 23 40 00 | 1292760
23 40 02 | Makeup Water Sys — Treatment | LS | 969570 | 1385100 | 1939140 | Decomposed from 23 40 00 | 969570
23 40 03 | Makeup Water Sys — Pumps | LS | 646380 | 923400 | 1292760 | Decomposed from 23 40 00 | 646380
23 40 04 | Makeup Water Sys — Controls | LS | 323190 | 461700 | 646380 | Decomposed from 23 40 00 | 323190
3 30 21 | Elevated Slabs — Concrete | LS | 1848000 | 2640000 | 3696000 | Decomposed from 03 30 20 | 1848000
3 30 22 | Elevated Slabs — Rebar | LS | 672000 | 960000 | 1344000 | Decomposed from 03 30 20 | 672000
3 30 23 | Elevated Slabs — Forming | LS | 504000 | 720000 | 1008000 | Decomposed from 03 30 20 | 504000
3 30 24 | Elevated Slabs — Finishing | LS | 336000 | 480000 | 672000 | Decomposed from 03 30 20 | 336000
26 06 11 | MV Cable — Cable | LS | 2047500 | 2925000 | 4095000 | Decomposed from 26 06 10 | 2047500
26 06 12 | MV Cable — Terminations | LS | 630000 | 900000 | 1260000 | Decomposed from 26 06 10 | 630000
26 06 13 | MV Cable — Testing | LS | 472500 | 675000 | 945000 | Decomposed from 26 06 10 | 472500
26 53 01 | Elec Cx — L1-2 Startup | LS | 1102500 | 1732500 | 2677500 | Decomposed from 26 53 00 | 1102500
26 53 02 | Elec Cx — L3 Functional | LS | 945000 | 1485000 | 2295000 | Decomposed from 26 53 00 | 945000
26 53 03 | Elec Cx — L4-5 Integrated | LS | 1102500 | 1732500 | 2677500 | Decomposed from 26 53 00 | 1102500
25 30 01 | MSI — Design | LS | 945000 | 1350000 | 1836000 | Decomposed from 25 30 00 | 945000
25 30 02 | MSI — Integration | LS | 1417500 | 2025000 | 2754000 | Decomposed from 25 30 00 | 1417500
25 30 03 | MSI — Test & Commission | LS | 787500 | 1125000 | 1530000 | Decomposed from 25 30 00 | 787500
23 09 01 | BMS — Controllers & Devices | LS | 1575000 | 2700000 | 4275000 | Decomposed from 23 09 00 | 1575000
23 09 02 | BMS — Software & Graphics | LS | 787500 | 1350000 | 2137500 | Decomposed from 23 09 00 | 787500
23 09 03 | BMS — Integration | LS | 787500 | 1350000 | 2137500 | Decomposed from 23 09 00 | 787500
21 31 01 | Fire Alarm — Panels & Devices | LS | 1760000 | 3080000 | 5280000 | Decomposed from 21 31 00 | 1760000
21 31 02 | Fire Alarm — Wiring | LS | 800000 | 1400000 | 2400000 | Decomposed from 21 31 00 | 800000
21 31 03 | Fire Alarm — Programming & Test | LS | 640000 | 1120000 | 1920000 | Decomposed from 21 31 00 | 640000
33 71 11 | MV Ductbank — Excavation & Conduit | LS | 1575000 | 2250000 | 3150000 | Decomposed from 33 71 10 | 1575000
33 71 12 | MV Ductbank — Concrete Encasement | LS | 945000 | 1350000 | 1890000 | Decomposed from 33 71 10 | 945000
33 71 13 | MV Ductbank — Manholes | LS | 630000 | 900000 | 1260000 | Decomposed from 33 71 10 | 630000
26 20 21 | Gen Exhaust — Silencers | LS | 1624218.75 | 2320312.5 | 3248437.5 | Decomposed from 26 20 20 | 1624218.75
26 20 22 | Gen Exhaust — Exhaust Piping | LS | 885937.5 | 1265625 | 1771875 | Decomposed from 26 20 20 | 885937.5
26 20 23 | Gen Exhaust — Supports & Install | LS | 442968.75 | 632812.5 | 885937.5 | Decomposed from 26 20 20 | 442968.75
3 30 81 | Mat Foundation — Concrete | LS | 1824000 | 2451000 | 3420000 | Decomposed from 03 30 80 | 1824000
3 30 82 | Mat Foundation — Rebar | LS | 760000 | 1021250 | 1425000 | Decomposed from 03 30 80 | 760000
3 30 83 | Mat Foundation — Forming & Finishing | LS | 456000 | 612750 | 855000 | Decomposed from 03 30 80 | 456000
26 32 51 | BESS — Battery Racks | LS | 1540000 | 2310000 | 3465000 | Decomposed from 26 32 50 | 1540000
26 32 52 | BESS — PCS / Inverters | LS | 700000 | 1050000 | 1575000 | Decomposed from 26 32 50 | 700000
26 32 53 | BESS — Controls & Install | LS | 560000 | 840000 | 1260000 | Decomposed from 26 32 50 | 560000
26 11 01 | Transformers — Units | LS | 1890000 | 3402000 | 5292000 | Decomposed from 26 11 00 | 1890000
26 11 02 | Transformers — Pads & Install | LS | 405000 | 729000 | 1134000 | Decomposed from 26 11 00 | 405000
26 11 03 | Transformers — Testing | LS | 405000 | 729000 | 1134000 | Decomposed from 26 11 00 | 405000
5 40 01 | CFMF — Studs & Track | LS | 1612800 | 2304000 | 3225600 | Decomposed from 05 40 00 | 1612800
5 40 02 | CFMF — Install | LS | 672000 | 960000 | 1344000 | Decomposed from 05 40 00 | 672000
5 40 03 | CFMF — Sheathing Attachment | LS | 403200 | 576000 | 806400 | Decomposed from 05 40 00 | 403200
21 13 01 | Pre-Action — Piping & Heads | LS | 1320000 | 2200000 | 3520000 | Decomposed from 21 13 00 | 1320000
21 13 02 | Pre-Action — Valves & Risers | LS | 792000 | 1320000 | 2112000 | Decomposed from 21 13 00 | 792000
21 13 03 | Pre-Action — Controls | LS | 528000 | 880000 | 1408000 | Decomposed from 21 13 00 | 528000
26 20 31 | Day Tanks — Tanks | LS | 1535625 | 2193750 | 3071250 | Decomposed from 26 20 30 | 1535625
26 20 32 | Day Tanks — Piping & Pumps | LS | 639843.75 | 914062.5 | 1279687.5 | Decomposed from 26 20 30 | 639843.75
26 20 33 | Day Tanks — Controls & Leak Detection | LS | 383906.25 | 548437.5 | 767812.5 | Decomposed from 26 20 30 | 383906.25
23 25 01 | Economizer — Heat Exchangers | LS | 1410750 | 2821500 | 4937625 | Decomposed from 23 25 00 | 1410750
23 25 02 | Economizer — Piping & Valves | LS | 641250 | 1282500 | 2244375 | Decomposed from 23 25 00 | 641250
23 25 03 | Economizer — Controls | LS | 513000 | 1026000 | 1795500 | Decomposed from 23 25 00 | 513000
26 40 11 | Interior Lighting — Fixtures | LS | 1478400 | 2112000 | 2956800 | Decomposed from 26 40 10 | 1478400
26 40 12 | Interior Lighting — Controls & Sensors | LS | 492800 | 704000 | 985600 | Decomposed from 26 40 10 | 492800
26 40 13 | Interior Lighting — Install & Wiring | LS | 492800 | 704000 | 985600 | Decomposed from 26 40 10 | 492800
23 36 01 | Humidification — Units | LS | 1478400 | 2112000 | 2956800 | Decomposed from 23 36 00 | 1478400
23 36 02 | Humidification — Distribution & Piping | LS | 616000 | 880000 | 1232000 | Decomposed from 23 36 00 | 616000
23 36 03 | Humidification — Controls | LS | 369600 | 528000 | 739200 | Decomposed from 23 36 00 | 369600
26 11 11 | UPS Input Xfmr — Units | LS | 1697850 | 2425500 | 3395700 | Decomposed from 26 11 10 | 1697850
26 11 12 | UPS Input Xfmr — Install | LS | 363825 | 519750 | 727650 | Decomposed from 26 11 10 | 363825
26 11 13 | UPS Input Xfmr — Testing | LS | 363825 | 519750 | 727650 | Decomposed from 26 11 10 | 363825
33 51 01 | Fuel Tanks — Tanks | LS | 1569375 | 2301750 | 3348000 | Decomposed from 33 51 00 | 1569375
33 51 02 | Fuel Tanks — Foundations & Containment | LS | 582187.5 | 853875 | 1242000 | Decomposed from 33 51 00 | 582187.5
33 51 03 | Fuel Tanks — Install & Testing | LS | 379687.5 | 556875 | 810000 | Decomposed from 33 51 00 | 379687.5
26 13 01 | ATS — Units | LS | 1606500 | 2295000 | 3213000 | Decomposed from 26 13 00 | 1606500
26 13 02 | ATS — Install | LS | 401625 | 573750 | 803250 | Decomposed from 26 13 00 | 401625
26 13 03 | ATS — Testing | LS | 354375 | 506250 | 708750 | Decomposed from 26 13 00 | 354375
23 09 11 | DCIM — Software & Sensors | LS | 1299375 | 1856250 | 2598750 | Decomposed from 23 09 10 | 1299375
23 09 12 | DCIM — Integration | LS | 590625 | 843750 | 1181250 | Decomposed from 23 09 10 | 590625
23 09 13 | DCIM — Install | LS | 472500 | 675000 | 945000 | Decomposed from 23 09 10 | 472500
9 97 01 | ESD Flooring — Material | LS | 1601600 | 2288000 | 3203200 | Decomposed from 09 97 00 | 1601600
9 97 02 | ESD Flooring — Install | LS | 616000 | 880000 | 1232000 | Decomposed from 09 97 00 | 616000
9 97 03 | ESD Flooring — Grounding | LS | 246400 | 352000 | 492800 | Decomposed from 09 97 00 | 246400
5 21 01 | Steel Joists — Joists | LS | 1528800 | 2184000 | 3057600 | Decomposed from 05 21 00 | 1528800
5 21 02 | Steel Joists — Erection | LS | 588000 | 840000 | 1176000 | Decomposed from 05 21 00 | 588000
5 21 03 | Steel Joists — Accessories | LS | 235200 | 336000 | 470400 | Decomposed from 05 21 00 | 235200
26 06 01 | MV Switchgear — Gear | LS | 1530000 | 2754000 | 4590000 | Decomposed from 26 06 00 | 1530000
26 06 02 | MV Switchgear — Breakers | LS | 450000 | 810000 | 1350000 | Decomposed from 26 06 00 | 450000
26 06 03 | MV Switchgear — Install & Testing | LS | 270000 | 486000 | 810000 | Decomposed from 26 06 00 | 270000
23 21 31 | CHW Piping (Sec) — Pipe & Fittings | LS | 1360800 | 1944000 | 2721600 | Decomposed from 23 21 30 | 1360800
23 21 32 | CHW Piping (Sec) — Valves & Specialties | LS | 567000 | 810000 | 1134000 | Decomposed from 23 21 30 | 567000
23 21 33 | CHW Piping (Sec) — Hangers & Install | LS | 340200 | 486000 | 680400 | Decomposed from 23 21 30 | 340200
23 05 01 | Mech Common — Hangers & Supports | LS | 1232000 | 1760000 | 2464000 | Decomposed from 23 05 00 | 1232000
23 05 02 | Mech Common — Sleeves & Seals | LS | 560000 | 800000 | 1120000 | Decomposed from 23 05 00 | 560000
23 05 03 | Mech Common — Misc | LS | 448000 | 640000 | 896000 | Decomposed from 23 05 00 | 448000
26 34 01 | Whips — Whips | LS | 1320000 | 2640000 | 4488000 | Decomposed from 26 34 00 | 1320000
26 34 02 | Whips — Connectors | LS | 550000 | 1100000 | 1870000 | Decomposed from 26 34 00 | 550000
26 34 03 | Whips — Install | LS | 330000 | 660000 | 1122000 | Decomposed from 26 34 00 | 330000
23 50 01 | TAB — Air Balancing | LS | 992250 | 1417500 | 1984500 | Decomposed from 23 50 00 | 992250
23 50 02 | TAB — Water Balancing | LS | 771750 | 1102500 | 1543500 | Decomposed from 23 50 00 | 771750
23 50 03 | TAB — Reporting | LS | 441000 | 630000 | 882000 | Decomposed from 23 50 00 | 441000
7 22 01 | Roof Insulation — Board | LS | 1568000 | 2240000 | 3136000 | Decomposed from 07 22 00 | 1568000
7 22 02 | Roof Insulation — Fasteners & Adhesive | LS | 403200 | 576000 | 806400 | Decomposed from 07 22 00 | 403200
7 22 03 | Roof Insulation — Install | LS | 268800 | 384000 | 537600 | Decomposed from 07 22 00 | 268800
5 12 21 | Gen Steel — Fabricated | LS | 1299375 | 1856250 | 2598750 | Decomposed from 05 12 20 | 1299375
5 12 22 | Gen Steel — Erection | LS | 606375 | 866250 | 1212750 | Decomposed from 05 12 20 | 606375
5 12 23 | Gen Steel — Coatings | LS | 259875 | 371250 | 519750 | Decomposed from 05 12 20 | 259875
26 27 51 | MCC — Units | LS | 1326000 | 1950000 | 2886000 | Decomposed from 26 27 50 | 1326000
26 27 52 | MCC — Breakers / Starters | LS | 448800 | 660000 | 976800 | Decomposed from 26 27 50 | 448800
26 27 53 | MCC — Install | LS | 265200 | 390000 | 577200 | Decomposed from 26 27 50 | 265200
25 50 01 | Facility Controls — Integration | LS | 1000000 | 1400000 | 1900000 | Decomposed from 25 50 00 | 1000000
25 50 02 | Facility Controls — Programming | LS | 600000 | 840000 | 1140000 | Decomposed from 25 50 00 | 600000
25 50 03 | Facility Controls — Testing | LS | 400000 | 560000 | 760000 | Decomposed from 25 50 00 | 400000
4 20 01 | CMU Walls — Block & Mortar | LS | 1267200 | 1612800 | 2073600 | Decomposed from 04 20 00 | 1267200
4 20 02 | CMU Walls — Reinforcing & Grout | LS | 528000 | 672000 | 864000 | Decomposed from 04 20 00 | 528000
4 20 03 | CMU Walls — Install | LS | 316800 | 403200 | 518400 | Decomposed from 04 20 00 | 316800
26 11 21 | Dry-Type Xfmr — Units | LS | 1389150 | 1984500 | 2778300 | Decomposed from 26 11 20 | 1389150
26 11 22 | Dry-Type Xfmr — Install | LS | 297675 | 425250 | 595350 | Decomposed from 26 11 20 | 297675
26 11 23 | Dry-Type Xfmr — Testing | LS | 297675 | 425250 | 595350 | Decomposed from 26 11 20 | 297675
25 90 01 | SOO — Development | LS | 990000 | 1440000 | 2025000 | Decomposed from 25 90 00 | 990000
25 90 02 | SOO — Documentation | LS | 495000 | 720000 | 1012500 | Decomposed from 25 90 00 | 495000
25 90 03 | SOO — Validation | LS | 495000 | 720000 | 1012500 | Decomposed from 25 90 00 | 495000
23 34 51 | Gen Vent — Fans | LS | 1089000 | 1633500 | 2425500 | Decomposed from 23 34 50 | 1089000
23 34 52 | Gen Vent — Ductwork & Louvers | LS | 594000 | 891000 | 1323000 | Decomposed from 23 34 50 | 594000
23 34 53 | Gen Vent — Controls | LS | 297000 | 445500 | 661500 | Decomposed from 23 34 50 | 297000
7 21 01 | Wall Insulation — Insulation | LS | 1310400 | 1872000 | 2620800 | Decomposed from 07 21 00 | 1310400
7 21 02 | Wall Insulation — Vapor Barrier | LS | 403200 | 576000 | 806400 | Decomposed from 07 21 00 | 403200
7 21 03 | Wall Insulation — Install | LS | 302400 | 432000 | 604800 | Decomposed from 07 21 00 | 302400
26 51 01 | Arc Flash — Relays | LS | 1039500 | 1485000 | 2079000 | Decomposed from 26 51 00 | 1039500
26 51 02 | Arc Flash — Settings & Study | LS | 472500 | 675000 | 945000 | Decomposed from 26 51 00 | 472500
26 51 03 | Arc Flash — Install | LS | 378000 | 540000 | 756000 | Decomposed from 26 51 00 | 378000
33 40 01 | Storm Drainage — Piping | LS | 1100000 | 2200000 | 3960000 | Decomposed from 33 40 00 | 1100000
33 40 02 | Storm Drainage — Structures (Inlets/MH) | LS | 600000 | 1200000 | 2160000 | Decomposed from 33 40 00 | 600000
33 40 03 | Storm Drainage — Install | LS | 300000 | 600000 | 1080000 | Decomposed from 33 40 00 | 300000
CX 02 00 | Level 1 Cx — Factory Witness Testing | MW | 35000 | 40250 | 47250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 35000
CX 03 00 | Level 2 Cx — Component Verification (Individual Equipment) | MW | 45000 | 51750 | 60750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 45000
CX 04 00 | Level 3 Cx — Subsystem Verification | MW | 55000 | 63250 | 74250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 55000
CX 05 00 | Level 4 Cx — System Verification (Integrated) | MW | 75000 | 86250 | 101250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 75000
CX 07 00 | Performance Verification Testing | MW | 65000 | 74750 | 87750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 65000
CX 08 00 | Seasonal Testing — Summer / Winter Peaks | MW | 45000 | 51750 | 60750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 45000
CX 09 00 | Failure Mode & Effects Testing (FMEA) | MW | 35000 | 40250 | 47250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 35000
CX 10 00 | Documentation — O&M Manuals, As-Builts | MW | 25000 | 28750 | 33750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 25000
CX 11 00 | Staff Training — Critical Systems Operation | MW | 18000 | 20700 | 24300 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 18000
CX 12 00 | Uptime Institute Tier Certification Support | LS | 250000 | 287500 | 337500 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 250000
CX 13 00 | Temporary Provisions — Load Banks for IST | MW | 35000 | 40250 | 47250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 35000
CX 14 00 | Deficiency Tracking & Remediation | MW | 25000 | 28750 | 33750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 25000
SC 02 00 | MEP Engineering — Critical Systems Design | MW | 225000 | 258750 | 303750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 225000
SC 03 00 | Structural Engineering | MW | 65000 | 74750 | 87750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 65000
SC 04 00 | Civil Engineering & Survey | MW | 35000 | 40250 | 47250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 35000
SC 05 00 | Geotechnical Investigation | EA | 125000 | 143750 | 168750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 125000
SC 06 00 | Environmental Consulting / Phase I ESA | LS | 250000 | 287500 | 337500 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 250000
SC 07 00 | Permitting & Entitlement Fees | MW | 85000 | 97750 | 114750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 85000
SC 08 00 | Utility Connection & Impact Fees | MW | 175000 | 201250 | 236250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 175000
SC 11 00 | LEED / Sustainability Certification | LS | 250000 | 287500 | 337500 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 250000
SC 12 00 | Owner's Representative / PM Fees | MO | 95000 | 109250 | 128250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 95000
SC 13 00 | Legal & Contract Administration | MO | 25000 | 28750 | 33750 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 25000
SC 14 00 | Cost Estimating / QS Services | MO | 35000 | 40250 | 47250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 35000
SC 16 00 | Third-Party Testing & Inspection (IOR) | MO | 55000 | 63250 | 74250 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 55000
SC 17 00 | FF&E — NOC / SOC / Office Fit-Out | SF | 175 | 201 | 236 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 175
SC 18 00 | Move Management & Logistics | LS | 350000 | 402500 | 472500 | Added from Construction Budget CX/SC section; Low = current budget basis (NoVA). | 350000
26 05 19 | Medium-Voltage Distribution — Building Unit Substations | EA | 185000 | 212750 | 249750 | Added scope — typical hyperscale allowance; Low = budget basis. | 185000
26 05 48 | Electrical Equipment Seismic Anchorage & Bracing | MW | 6500 | 7475 | 8775 | Added scope — typical hyperscale allowance; Low = budget basis. | 6500
26 05 53 | Electrical Identification & Arc-Flash Labeling | SF | 0.15 | 0.17 | 0.2 | Added scope — typical hyperscale allowance; Low = budget basis. | 0.15
26 05 90 | Temporary Construction Power & Distribution | MW | 12000 | 13800 | 16200 | Added scope — typical hyperscale allowance; Low = budget basis. | 12000
26 05 99 | Electrical Spare Parts & Maintenance Stock | MW | 4500 | 5175 | 6075 | Added scope — typical hyperscale allowance; Low = budget basis. | 4500
26 20 50 | Generator Radiators / Remote Cooling Systems | EA | 35000 | 40250 | 47250 | Added scope — typical hyperscale allowance; Low = budget basis. | 35000
26 20 60 | Generator Fuel Polishing / Filtration System | EA | 18000 | 20700 | 24300 | Added scope — typical hyperscale allowance; Low = budget basis. | 18000
26 20 70 | Generator Emissions Control (SCR / Tier 4) | kW | 25 | 28.75 | 33.75 | Added scope — typical hyperscale allowance; Low = budget basis. | 25
23 63 00 | Dry Coolers / Fluid Coolers — Free Cooling | TON | 185 | 212.75 | 249.75 | Added scope — typical hyperscale allowance; Low = budget basis. | 185
23 09 60 | Mechanical Leak Detection — Chilled Water & Under-Floor | SF | 0.45 | 0.52 | 0.61 | Added scope — typical hyperscale allowance; Low = budget basis. | 0.45
23 05 80 | Mechanical Equipment Vibration Isolation | MW | 4500 | 5175 | 6075 | Added scope — typical hyperscale allowance; Low = budget basis. | 4500
23 21 70 | CW/CHW Pipe Freeze Protection / Heat Trace | LF | 22 | 25.3 | 29.7 | Added scope — typical hyperscale allowance; Low = budget basis. | 22
23 31 60 | Acoustic Louvers & Sound Attenuation | MW | 3500 | 4025 | 4725 | Added scope — typical hyperscale allowance; Low = budget basis. | 3500
27 08 00 | Communications Commissioning & Acceptance Testing | MW | 3500 | 4025 | 4725 | Added scope — typical hyperscale allowance; Low = budget basis. | 3500
27 10 50 | Pre-Terminated MPO/MTP Trunk Cabling | EA | 145 | 166.75 | 195.75 | Added scope — typical hyperscale allowance; Low = budget basis. | 145
27 11 50 | Campus / OSP Fiber Backbone — Inter-Building (SM) | LF | 18 | 20.7 | 24.3 | Added scope — typical hyperscale allowance; Low = budget basis. | 18
27 13 50 | Horizontal Distribution Area (HDA) Buildout | EA | 12500 | 14375 | 16875 | Added scope — typical hyperscale allowance; Low = budget basis. | 12500
31 09 00 | Geotechnical Instrumentation & Monitoring | EA | 8500 | 9775 | 11475 | Added scope — typical hyperscale allowance; Low = budget basis. | 8500
33 46 00 | Subdrainage / Under-Slab Drainage System | SF | 0.35 | 0.4 | 0.47 | Added scope — typical hyperscale allowance; Low = budget basis. | 0.35
22 66 00 | Emergency Eyewash & Safety Showers — Battery Rooms | EA | 4500 | 5175 | 6075 | Added scope — typical hyperscale allowance; Low = budget basis. | 4500
09 67 00 | Epoxy / Resinous Floor Coating — MEP & BOH | SF | 9 | 10.35 | 12.15 | Added scope — typical hyperscale allowance; Low = budget basis. | 9
32 31 50 | Security Gates & Crash-Rated Barriers (K-Rated) | EA | 85000 | 97750 | 114750 | Added scope — typical hyperscale allowance; Low = budget basis. | 85000
28 23 50 | Video Analytics / AI Surveillance Platform | MW | 2500 | 2875 | 3375 | Added scope — typical hyperscale allowance; Low = budget basis. | 2500
28 13 70 | Visitor Management System | EA | 35000 | 40250 | 47250 | Added scope — typical hyperscale allowance; Low = budget basis. | 35000
03 39 00 | Concrete Curing & Sealing Compounds | SF | 0.65 | 0.75 | 0.88 | Added scope — typical hyperscale allowance; Low = budget basis. | 0.65
08 56 00 | Blast-Resistant / Security Windows | EA | 4500 | 5175 | 6075 | Added scope — typical hyperscale allowance; Low = budget basis. | 4500
22 34 00 | Domestic Water Heaters | EA | 9500 | 10925 | 12825 | Added scope — typical hyperscale allowance; Low = budget basis. | 9500
09 84 00 | Acoustic Wall Treatment Panels | SF | 16 | 18.4 | 21.6 | Added scope — typical hyperscale allowance; Low = budget basis. | 16
10 51 00 | Staff Lockers & Equipment | EA | 350 | 402.5 | 472.5 | Added scope — typical hyperscale allowance; Low = budget basis. | 350
23 81 00 | Packaged DX Units — Electrical / Admin Rooms | TON | 1200 | 1380 | 1620 | Added scope — typical hyperscale allowance; Low = budget basis. | 1200
Note on I1: Kevin: Linked to Scenario & Presets!B15 (active Pricing Tier). Drives the Selected Price column (H) via CHOOSE/MATCH.

## Allowances & Alternates
DATA CENTER — ALLOWANCES & ALTERNATES
ALLOWANCES
# | Description | CSI Div | Allowance Amt | Actual Cost | Variance | Status | Vendor | Notes
1 | Owner-Furnished Equipment Allowance | 27 | 2500000 | 0 | 2500000 | Pending
2 | Fiber Optic Entrance — Carrier Buildout | 27 | 1200000 | 0 | 1200000 | Pending
3 | Office / NOC Furniture | 10 | 850000 | 0 | 850000 | Pending
4 | Landscaping Allowance | 32 | 350000 | 0 | 350000 | Pending
5 | Security System Enhancements | 28 | 750000 | 0 | 750000 | Pending
6 | Generator Fuel Fill — Initial | 33 | 425000 | 0 | 425000 | Pending
7 | Contingency (suppressed — included in budget lines) | 1 | 0 | 0 | 0 | Pending
8 | IT Cabinet Accessories | 27 | 500000 | 0 | 500000 | Pending
9 | Commissioning & Integrated Systems Testing (L1–L5 IST) | 1 | 1800000 | 0 | 1800000 | Pending |  | L5 integrated systems test across electrical/mechanical; pull/fail testing
10 | DCIM & Building Management System Integration | 25 | 900000 | 0 | 900000 | Pending |  | DCIM platform, BMS graphics/programming, sensor integration
11 | Structured Cabling Backbone (MMR / MDA / Cross-Connect) | 27 | 1500000 | 0 | 1500000 | Pending |  | OS2 fiber backbone, Cat6A, cross-connect fields in MMR/MDA
12 | Clean-Agent Fire Suppression & VESDA Detection | 21 | 1100000 | 0 | 1100000 | Pending |  | Inert/clean-agent in data halls; VESDA aspirating smoke detection
13 | Grounding, Bonding & Lightning Protection | 26 | 650000 | 0 | 650000 | Pending |  | Signal reference grid, telecom bonding backbone, LPS air terminals
14 | Critical Spare Parts & Maintenance Inventory | 23 | 1250000 | 0 | 1250000 | Pending |  | OEM spares for CRAH/CRAC, breakers, pumps, UPS modules
15 | Utility Interconnection & Substation Fees | 33 | 2200000 | 0 | 2200000 | Pending |  | Utility interconnection, primary switchgear/substation contributions
16 | Signage, Wayfinding & ADA Compliance | 10 | 175000 | 0 | 175000 | Pending |  | Code/arc-flash signage, room ID, ADA wayfinding
17 | Temporary Construction Power & Conditioning | 1 | 600000 | 0 | 600000 | Pending |  | Temp power, generators, distribution for construction phase
18 | Hazmat Abatement / Unforeseen Site Conditions | 2 | 800000 | 0 | 800000 | Pending |  | Abatement, dewatering, rock/soil remediation contingency
| TOTAL ALLOWANCES |  | 17550000 | 0 | 17550000
ALTERNATES — TIER UPGRADES & OPTIONS
Alt # | Description | CSI Div | Baseline Cost | Upgrade Cost | Net Add ($) | Accepted? | Tier Impact | Notes
ALT-01 | Tier III → Tier IV Electrical (2N UPS/Gen) | 26 | 217800000 | 326700000 | 108900000 | No | Tier IV
ALT-02 | Tier III → Tier IV Mechanical (2N Cooling) | 23 | 2074286 | 18500000 | 16425714 | No | Tier IV
ALT-03 | Liquid Cooling Infrastructure (in lieu of air) | 23 | 0 | 8500000 | 8500000 | No | Tier III/IV
ALT-04 | On-Site Renewable — Solar Canopy | 26 | 0 | 12000000 | 12000000 | No | None
ALT-05 | Battery Energy Storage System (BESS) | 26 | 9199228 | 15800000 | 6600772 | No | Tier III/IV
ALT-06 | Lithium-Ion UPS Batteries (vs. VRLA) | 26 | 6222857 | 4200000 | -2022857 | No | None
ALT-07 | Free Cooling — Airside Economizer | 23 | 16830000 | 21500000 | 4670000 | No | None
ALT-08 | Enhanced Physical Security — Anti-Ram | 28 | 12588417 | 14200000 | 1611583 | No | None
ALT-09 | Generator — Natural Gas (vs. Diesel) | 26 | 7882286 | 12500000 | 4617714 | No | None
ALT-10 | High-Density Cooling (30+ kW/rack) | 23 | 990000000 | 880000000 | -110000000 | No | None
ALT-11 | Modular / Prefab Data Hall Pod | All | 475200 | 1850000 | 1374800 | No | Tier II/III
ALT-12 | Additional Meet-Me Room / Carrier Entrance | 27 | 0 | 0 | 0 | No | None
| TOTAL ACCEPTED ALTERNATES |  |  |  | 0
SUMMARY
| Total Allowances: |  |  |  | 17550000
| Total Accepted Alternates: |  |  |  | 0
| Combined Net Impact (Allowances + Accepted Alts): |  |  |  | 17550000
| ACCEPTED ALTERNATES (for Proposal): |  |  |  |  | 0
Note on D11: Kevin: Zeroed — contingency is already embedded in every Construction Budget H-column line item. Keeping a separate allowance line would triple-count.

## Location Factors
DATA CENTER — LOCATION ADJUSTMENT FACTORS
Selected Market: | Northern Virginia
Baseline Market: | Northern Virginia (Index = 1.00)
MASTER LOCATION FACTOR: | 1
Selected Region / Country: | North America · United States
CATEGORY ADJUSTMENT FACTORS
Category | Base Factor | Category Adj. | Combined Factor | Notes
Site Work | 1 | 0% | 1 | Earthwork, paving, utilities, fencing
Concrete | 1 | 0% | 1 | Foundations, slabs, precast
Structural Steel | 1 | 2% | 1.02 | Steel erection, decking, misc metals
Building Envelope | 1 | 0% | 1 | Roofing, wall panels, waterproofing
Plumbing | 1 | 0% | 1 | Domestic water, make-up water, drains
Fire Suppression | 1 | 3% | 1.03 | Clean agent, sprinkler, VESDA, alarm
HVAC / Cooling | 1 | 5% | 1.05 | Chillers, CRAHs, towers, piping, controls
Electrical / Critical Power | 1 | 6% | 1.06 | Switchgear, generators, UPS, PDUs
IT Infrastructure | 1 | 0% | 1 | Cabling, racks, DCIM, leak detection
Communications | 1 | 0% | 1 | Cabling, cabinets, DCIM, leak detection
Security | 1 | 5% | 1.05 | Access control, CCTV, intrusion detection
Commissioning | 1 | 8% | 1.08 | L1-L5 Cx, IST, seasonal, FMEA
Openings | 1 | 0 | 1 | Doors, frames, hardware, glazing, overhead doors
Finishes | 1 | 0 | 1 | Drywall, paint, raised floor, ACT, flooring
Specialties | 1 | 0 | 1 | Signage, lockers, partitions, fire extinguishers
General Conditions | 1 | 0% | 1 | PM, temp facilities, QA/QC, permits
Soft Costs | 1 | -2% | 0.98 | A/E fees, CxA, Uptime cert, BIM, legal
MARKET INDEX TABLE
Market | Region | Factor | State | Country
Northern Virginia | North America | 1 | VA | United States
Albuquerque, NM | North America | 0.86 | NM | United States
Atlanta | North America | 0.86 | GA | United States
Austin, TX | North America | 0.9 | TX | United States
Baltimore, MD | North America | 0.98 | MD | United States
Birmingham, AL | North America | 0.82 | AL | United States
Boise, ID | North America | 0.88 | ID | United States
Boston, MA | North America | 1.24 | MA | United States
Buffalo, NY | North America | 1.03 | NY | United States
Charlotte, NC | North America | 0.85 | NC | United States
Chicago | North America | 1.05 | IL | United States
Cincinnati, OH | North America | 0.95 | OH | United States
Cleveland, OH | North America | 0.98 | OH | United States
Columbus / New Albany | North America | 0.89 | OH | United States
Dallas / Fort Worth | North America | 0.87 | TX | United States
Denver, CO | North America | 0.99 | CO | United States
Des Moines, IA | North America | 0.92 | IA | United States
Detroit, MI | North America | 1.02 | MI | United States
El Paso, TX | North America | 0.8 | TX | United States
Fresno, CA | North America | 1.05 | CA | United States
Grand Rapids, MI | North America | 0.93 | MI | United States
Hartford, CT | North America | 1.07 | CT | United States
Honolulu, HI | North America | 1.27 | HI | United States
Houston, TX | North America | 0.89 | TX | United States
Indianapolis, IN | North America | 0.93 | IN | United States
Inland Empire / Riverside, CA | North America | 1.08 | CA | United States
Jacksonville, FL | North America | 0.84 | FL | United States
Kansas City, MO | North America | 0.95 | MO | United States
Las Vegas, NV | North America | 1 | NV | United States
Los Angeles, CA | North America | 1.15 | CA | United States
Louisville, KY | North America | 0.91 | KY | United States
Memphis, TN | North America | 0.84 | TN | United States
Miami / Fort Lauderdale, FL | North America | 0.92 | FL | United States
Milwaukee, WI | North America | 1.04 | WI | United States
Minneapolis / St. Paul, MN | North America | 1.05 | MN | United States
Nashville, TN | North America | 0.87 | TN | United States
New Orleans, LA | North America | 0.88 | LA | United States
New York / Newark, NY-NJ | North America | 1.4 | NY | United States
Oklahoma City, OK | North America | 0.83 | OK | United States
Omaha, NE | North America | 0.9 | NE | United States
Orlando, FL | North America | 0.85 | FL | United States
Philadelphia, PA | North America | 1.18 | PA | United States
Phoenix / Mesa | North America | 0.88 | AZ | United States
Pittsburgh, PA | North America | 1.01 | PA | United States
Portland / Hillsboro | North America | 1.02 | OR | United States
Providence, RI | North America | 1.07 | RI | United States
Raleigh / Durham, NC | North America | 0.86 | NC | United States
Reno, NV | North America | 0.98 | NV | United States
Richmond, VA | North America | 0.91 | VA | United States
Rochester, NY | North America | 1.01 | NY | United States
Sacramento, CA | North America | 1.09 | CA | United States
Salt Lake City | North America | 0.84 | UT | United States
San Antonio, TX | North America | 0.85 | TX | United States
San Diego, CA | North America | 1.11 | CA | United States
San Francisco / Oakland, CA | North America | 1.36 | CA | United States
Seattle / Tacoma, WA | North America | 1.17 | WA | United States
Silicon Valley | North America | 1.28 | CA | United States
St. Louis, MO | North America | 0.97 | MO | United States
Tampa / St. Petersburg, FL | North America | 0.85 | FL | United States
Tucson, AZ | North America | 0.86 | AZ | United States
Tulsa, OK | North America | 0.82 | OK | United States
Virginia Beach / Norfolk, VA | North America | 0.88 | VA | United States
Toronto | North America | 1.12 |  | Canada
Montreal | North America | 1.02 |  | Canada
London | Europe | 1.35 |  | United Kingdom
Frankfurt | Europe | 1.22 |  | Germany
Amsterdam | Europe | 1.18 |  | Netherlands
Dublin | Europe | 1.15 |  | Ireland
Paris | Europe | 1.3 |  | France
Stockholm | Europe | 1.25 |  | Sweden
Singapore | Asia-Pacific | 1.2 |  | Singapore
Tokyo | Asia-Pacific | 1.4 |  | Japan
Sydney | Asia-Pacific | 1.18 |  | Australia
Mumbai | Asia-Pacific | 0.55 |  | India
Carson City, NV | North America | 1.01 | NV | United States
Eagle Pass, TX | North America | 0.79 | TX | United States
Enid, OK | North America | 0.81 | OK | United States
Walla Walla, WA | North America | 0.97 | WA | United States
Lewiston, ID-WA | North America | 0.85 | ID | United States
Minot, ND | North America | 0.99 | ND | United States
Grand Island, NE | North America | 0.87 | NE | United States
Casper, WY | North America | 0.96 | WY | United States
Elmira, NY | North America | 0.99 | NY | United States
Midland, MI | North America | 0.93 | MI | United States
Kokomo, IN | North America | 0.89 | IN | United States
Great Falls, MT | North America | 0.95 | MT | United States
Columbus, IN | North America | 0.89 | IN | United States
Parkersburg–Vienna, WV | North America | 0.92 | WV | United States
Grants Pass, OR | North America | 1.03 | OR | United States
Hinesville, GA | North America | 0.8 | GA | United States
Pocatello, ID | North America | 0.9 | ID | United States
Fairbanks–College, AK | North America | 1.38 | AK | United States
Helena, MT | North America | 0.96 | MT | United States
Cape Girardeau, MO-IL | North America | 0.92 | MO | United States
Corvallis, OR | North America | 1.02 | OR | United States
Victoria, TX | North America | 0.83 | TX | United States
Dubuque, IA | North America | 0.89 | IA | United States
Hot Springs, AR | North America | 0.76 | AR | United States
Decatur, IL | North America | 0.94 | IL | United States
Lima, OH | North America | 0.91 | OH | United States
Rome, GA | North America | 0.81 | GA | United States
Cheyenne, WY | North America | 0.94 | WY | United States
Paducah, KY-IL | North America | 0.86 | KY | United States
Bay City, MI | North America | 0.93 | MI | United States
Gadsden, AL | North America | 0.76 | AL | United States
Grand Forks, ND-MN | North America | 0.97 | ND | United States
Fond du Lac, WI | North America | 0.96 | WI | United States
Sumter, SC | North America | 0.78 | SC | United States
Mankato, MN | North America | 0.97 | MN | United States
Ithaca, NY | North America | 1.06 | NY | United States
Kankakee, IL | North America | 0.94 | IL | United States
Gettysburg, PA | North America | 0.96 | PA | United States
Pinehurst–Southern Pines, NC | North America | 0.9 | NC | United States
Sebring, FL | North America | 0.88 | FL | United States
Beckley, WV | North America | 0.92 | WV | United States
Michigan City–La Porte, IN | North America | 0.89 | IN | United States
Muncie, IN | North America | 0.89 | IN | United States
Watertown–Fort Drum, NY | North America | 0.99 | NY | United States
Williamsport, PA | North America | 0.96 | PA | United States
Weirton–Steubenville, WV-OH | North America | 0.92 | WV | United States
Sandusky, OH | North America | 0.91 | OH | United States
Owensboro, KY | North America | 0.86 | KY | United States
Longview–Kelso, WA | North America | 0.97 | WA | United States
Lewiston–Auburn, ME | North America | 0.95 | ME | United States
Anniston–Oxford, AL | North America | 0.76 | AL | United States
Brunswick–St. Simons, GA | North America | 0.89 | GA | United States
Sheboygan, WI | North America | 0.96 | WI | United States
St. Joseph, MO-KS | North America | 0.92 | MO | United States
Altoona, PA | North America | 0.96 | PA | United States
Goldsboro, NC | North America | 0.8 | NC | United States
Farmington, NM | North America | 0.89 | NM | United States
San Angelo, TX | North America | 0.83 | TX | United States
Lawrence, KS | North America | 0.9 | KS | United States
Twin Falls, ID | North America | 0.9 | ID | United States
Mansfield, OH | North America | 0.91 | OH | United States
Glens Falls, NY | North America | 1.04 | NY | United States
Sierra Vista–Douglas, AZ | North America | 0.89 | AZ | United States
Lawton, OK | North America | 0.79 | OK | United States
Morristown, TN | North America | 0.82 | TN | United States
Bozeman, MT | North America | 1.01 | MT | United States
Wenatchee–East Wenatchee, WA | North America | 1.03 | WA | United States
Missoula, MT | North America | 0.97 | MT | United States
Elizabethtown, KY | North America | 0.86 | KY | United States
Staunton–Stuarts Draft, VA | North America | 0.89 | VA | United States
Pittsfield, MA | North America | 1.22 | MA | United States
Ames, IA | North America | 0.94 | IA | United States
Johnstown, PA | North America | 0.96 | PA | United States
Salisbury, MD | North America | 0.94 | MD | United States
Cleveland, TN | North America | 0.83 | TN | United States
Albany, OR | North America | 0.96 | OR | United States
Napa, CA | North America | 1.19 | CA | United States
Mount Vernon–Anacortes, WA | North America | 1.04 | WA | United States
Battle Creek, MI | North America | 0.93 | MI | United States
Manhattan, KS | North America | 0.9 | KS | United States
Springfield, OH | North America | 0.91 | OH | United States
Wheeling, WV-OH | North America | 0.92 | WV | United States
Jonesboro, AR | North America | 0.76 | AR | United States
Harrisonburg, VA | North America | 0.94 | VA | United States
Wausau, WI | North America | 0.96 | WI | United States
Bismarck, ND | North America | 0.97 | ND | United States
Hammond, LA | North America | 0.83 | LA | United States
Morgantown, WV | North America | 0.97 | WV | United States
Flagstaff, AZ | North America | 0.93 | AZ | United States
Lebanon, PA | North America | 0.96 | PA | United States
Albany, GA | North America | 0.8 | GA | United States
Texarkana, TX-AR | North America | 0.81 | TX | United States
Sioux City, IA-NE-SD | North America | 0.89 | IA | United States
Dalton, GA | North America | 0.81 | GA | United States
Rocky Mount, NC | North America | 0.8 | NC | United States
Alexandria, LA | North America | 0.83 | LA | United States
Winchester, VA-WV | North America | 0.89 | VA | United States
Wichita Falls, TX | North America | 0.83 | TX | United States
Sherman–Denison, TX | North America | 0.83 | TX | United States
Jefferson City, MO | North America | 0.92 | MO | United States
STATE CONSTRUCTION COST FACTORS — MODELED REFERENCE (not linked; Northern Virginia = 1.00)
State | Factor
AK | 1.25
AL | 0.82
AR | 0.8
AZ | 0.87
CA | 1.08
CO | 0.99
CT | 1.07
DE | 1
FL | 0.86
GA | 0.85
HI | 1.27
IA | 0.92
ID | 0.88
IL | 0.97
IN | 0.92
KS | 0.88
KY | 0.9
LA | 0.87
MA | 1.18
MD | 0.97
ME | 0.98
MI | 0.96
MN | 1
MO | 0.95
MS | 0.8
MT | 0.92
NC | 0.85
ND | 0.95
NE | 0.9
NH | 1
NJ | 1.2
NM | 0.86
NV | 0.98
NY | 1.02
OH | 0.94
OK | 0.83
OR | 0.99
PA | 0.99
RI | 1.07
SC | 0.83
SD | 0.88
TN | 0.86
TX | 0.86
UT | 0.84
VA | 0.92
VT | 1
WA | 1
WI | 0.99
WV | 0.95
WY | 0.92
Note on A30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Relative construction-cost location factors, Northern Virginia = 1.00 baseline. Planning-level estimates from regional construction cost indices; refine with local RSMeans / contractor data before GMP.
Note on A206: Kevin: Modeled construction cost factors indexed to Northern Virginia = 1.00, derived from state-level RSMeans-style cost relativities and anchored to the major-market factors already in this table (e.g., Boston 1.24, NYC 1.40, Dallas 0.87). Estimates only — replace with project-specific City Cost Index (RSMeans/ENR) when available. Small-metro costs typically run a few points below the state's large-metro average.
Note on C30: Kevin: Rows 31-104: established major-market factors. Rows 105-204 (bottom-100 MSAs): city-based construction cost factors, indexed to Northern Virginia = 1.00. Modeled estimates = state base x local city adjustment (remoteness/resort > 1.0; low-cost South/border < 1.0). State-level basis retained in the 'State Construction Cost Factors' table below (rows 206-257). Replace with project-specific City Cost Index (RSMeans/ENR) when available.

## Value Engineering
VALUE ENGINEERING LOG
VE proposals — pricing, status, and decision rationale. Items marked Accepted flow into the budget; Pending items are reviewed at the next milestone.
# | ID | Description | Division | Building | Baseline Cost | Proposed Cost | Savings ($) | Savings (%) | Schedule Impact | Quality / Risk | Status | Decision Date | Owner
1 | VE-001 | Tilt-up panels in lieu of CMU exterior wall | 7 | All Buildings | 1786466 | 1450000 | 336466 | 18.83% | Saves 2 weeks | Low — proven tilt-up method for DC | Accepted
2 | VE-002 | Reduce slab thickness in admin building | 3 | All Buildings | 4500000 | 3825000 | 675000 | 15% | None | Low — admin area only, not data halls | Accepted
3 | VE-003 | Single-source steel package across campus | 5 | Shared | 34650000 | 32200000 | 2450000 | 7.071% | Saves 3 weeks | Med — single-source risk; bond required | Accepted
4 | VE-004 | Defer landscaping to post-occupancy | 32 | Shared | 528000 | 0 | 0 | 0% | None | Low — deferred to post-CO, cosmetic only | Accepted
5 | VE-005 | Standardize door hardware across all buildings | 8 | Shared | 409398 | 365000 | 44398 | 10.84% | None | Low — reduces procurement complexity | Accepted
6 | VE-006 | Overhead busway in lieu of conduit + cable whips (data halls) | 26 | All Buildings | 24000000 | 19500000 | 4500000 | 18.75% | Saves time | Low risk | Accepted
7 | VE-007 | Air-cooled chillers; eliminate cooling towers + CW treatment | 23 | All Buildings | 47500000 | 41000000 | 6500000 | 13.68% | +0 days | Med risk | Pending
8 | VE-008 | Prefabricated electrical skids (modular PDU / RPP) | 26 | All Buildings | 18000000 | 15200000 | 2800000 | 15.56% | Saves time | Low risk | Accepted
9 | VE-009 | VRF for office / admin in lieu of chilled-water AHUs | 23 | Shared | 3200000 | 2400000 | 800000 | 25% | +0 days | Low risk | Accepted
10 | VE-010 | Consolidate IT MDA / IDA rooms (reduce cabling runs) | 27 | All Buildings | 12000000 | 10300000 | 1700000 | 14.17% | +0 days | Low risk | Accepted
11 | VE-011 | Eliminate raised access floor; overhead power & cooling distribution | 3 | All Buildings | 18000000 | 14500000 | 3500000 | 19.44% | Saves 1 week | Low — overhead distribution proven in DC | Accepted
12 | VE-012 | Aluminum feeders & busway in lieu of copper | 26 | All Buildings | 38000000 | 31000000 | 7000000 | 18.42% | None | Med — Al terminations/derating per NEC | Accepted
13 | VE-013 | Medium-voltage reticulation to data halls (reduce LV copper/gear) | 26 | Shared | 26000000 | 22000000 | 4000000 | 15.38% | Saves 1 week | Med — MV switching/safety training | Accepted
14 | VE-014 | Reduce UPS battery autonomy (10 → 5 min) | 26 | All Buildings | 14000000 | 9500000 | 4500000 | 32.14% | None | High — resiliency: less UPS ride-through to generator start | Pending
15 | VE-015 | Reduce chilled-water plant redundancy (N+2 → N+1) | 23 | Shared | 42000000 | 34000000 | 8000000 | 19.05% | Saves 2 weeks | High — resiliency: lower cooling redundancy (N+2 → N+1) | Pending
16 | VE-016 | Raise supply-air / CHW setpoints (ASHRAE A1→A3); downsize cooling | 23 | All Buildings | 30000000 | 26500000 | 3500000 | 11.67% | None | Low — within ASHRAE TC9.9 envelope | Accepted
17 | VE-017 | Right-size standby generation (N+1 vs 2N) | 26 | Shared | 60000000 | 48000000 | 12000000 | 20% | Saves 3 weeks | High — resiliency: reduced power redundancy (N+1 vs 2N) | Pending
18 | VE-018 | Single-vendor standardized switchgear package | 26 | All Buildings | 22000000 | 19800000 | 2200000 | 10% | Saves 2 weeks | Med — single-source; bond required | Accepted
19 | VE-019 | Exposed structure; minimize data-hall finishes | 9 | All Buildings | 6000000 | 4200000 | 1800000 | 30% | Saves 1 week | Low — cosmetic; back-of-house only | Accepted
20 | VE-020 | Reduce on-site generator fuel storage (24h → 12h) | 23 | Shared | 8500000 | 6000000 | 2500000 | 29.41% | None | High — resiliency: shorter on-site fuel autonomy (24h → 12h) | Pending
|  | TOTALS |  |  | 411073864 | 341740000 | 68805864 | 16.74%
VE STATUS SUMMARY
Accepted | Count: | 15 | Savings: | 35305864
Pending / Review | Count: | 5 | Savings: | 33500000
Rejected | Count: | 0 | Savings: | 0
VE-ADJUSTED ESTIMATE (active VE scenario — see selector →)
Base Estimate (live scenario): |  |  |  | 1088341827.0674
Less: VE Savings (active scenario): |  |  |  | 35305864
VE-Adjusted Total: |  |  |  | 1053035963.0674
VE-Adjusted Cost / MW: |  |  |  | 11700399.5896
VE SCENARIO MODEL — ADOPTION SCENARIOS | [8 empty] | ACTIVE VE SCENARIO
Toggle which VE items each scenario accepts: 1 (✓) = accept, 0 (–) = reject. Aggressive takes every cost lever that PRESERVES resiliency; Accept All additionally adopts the four High-risk resiliency reductions (UPS autonomy, cooling & power redundancy, fuel storage). | [8 empty] | Selected scenario: |  | Balanced
| ID | Description | Risk | As-Designed | Conservative | Balanced | Aggressive | Accept All | Items accepted: |  | 15
| VE-001 | Tilt-up panels in lieu of CMU exterior wall | Low | 0 | 1 | 1 | 1 | 1 | VE savings ($): |  | 35305864
| VE-002 | Reduce slab thickness in admin building | Low | 0 | 1 | 1 | 1 | 1 | VE-adjusted total: |  | 1053035963.0674
| VE-003 | Single-source steel package across campus | Med | 0 | 0 | 1 | 1 | 1 | VE-adjusted $/MW: |  | 11700399.5896
| VE-004 | Defer landscaping to post-occupancy | Low | 0 | 1 | 1 | 1 | 1 | Reduction vs base: |  | 3.244%
| VE-005 | Standardize door hardware across all buildings | Low | 0 | 1 | 1 | 1 | 1 | Med-risk items incl.: |  | 4
| VE-006 | Overhead busway in lieu of conduit + cable whips (data halls) | Low | 0 | 1 | 1 | 1 | 1 | Resiliency cuts incl.: |  | 0
| VE-007 | Air-cooled chillers; eliminate cooling towers + CW treatment | Med | 0 | 0 | 0 | 1 | 1
| VE-008 | Prefabricated electrical skids (modular PDU / RPP) | Low | 0 | 1 | 1 | 1 | 1
| VE-009 | VRF for office / admin in lieu of chilled-water AHUs | Low | 0 | 1 | 1 | 1 | 1
| VE-010 | Consolidate IT MDA / IDA rooms (reduce cabling runs) | Low | 0 | 1 | 1 | 1 | 1
| VE-011 | Eliminate raised access floor; overhead power & cooling distribution | Low | 0 | 1 | 1 | 1 | 1
| VE-012 | Aluminum feeders & busway in lieu of copper | Med | 0 | 0 | 1 | 1 | 1
| VE-013 | Medium-voltage reticulation to data halls (reduce LV copper/gear) | Med | 0 | 0 | 1 | 1 | 1
| VE-014 | Reduce UPS battery autonomy (10 → 5 min) | High | 0 | 0 | 0 | 0 | 1
| VE-015 | Reduce chilled-water plant redundancy (N+2 → N+1) | High | 0 | 0 | 0 | 0 | 1
| VE-016 | Raise supply-air / CHW setpoints (ASHRAE A1→A3); downsize cooling | Low | 0 | 1 | 1 | 1 | 1
| VE-017 | Right-size standby generation (N+1 vs 2N) | High | 0 | 0 | 0 | 0 | 1
| VE-018 | Single-vendor standardized switchgear package | Med | 0 | 0 | 1 | 1 | 1
| VE-019 | Exposed structure; minimize data-hall finishes | Low | 0 | 1 | 1 | 1 | 1
| VE-020 | Reduce on-site generator fuel storage (24h → 12h) | High | 0 | 0 | 0 | 0 | 1
SCENARIO ROLL-UP
Items accepted (count) |  |  |  | 0 | 11 | 15 | 16 | 20
Total VE savings ($) |  |  |  | 0 | 19655864 | 35305864 | 41805864 | 68805864
VE-adjusted total ($) |  |  |  | 1088341827.0674 | 1068685963.0674 | 1053035963.0674 | 1046535963.0674 | 1019535963.0674
VE-adjusted $ / MW |  |  |  | 12092686.9674 | 11874288.4785 | 11700399.5896 | 11628177.3674 | 11328177.3674
Reduction vs base (%) |  |  |  | 0% | 1.806% | 3.244% | 3.841% | 6.322%
Med-risk items included |  |  |  | 0 | 0 | 4 | 5 | 5
Resiliency cuts included (High) |  |  |  | 0 | 0 | 0 | 0 | 4

## Basis of Estimate
BASIS OF ESTIMATE (BOE)
Project: | Data Center Template, Northern Virginia |  | Estimate Class: | Class 3 (DD)
Estimate Date: | 2026-05-01 |  | Accuracy Range: | −20% / +30%
Prepared By: | Senior Cost Estimator |  | Reviewed By: | Estimating Lead
Cost Manager:
1. DOCUMENTS REVIEWED
Drawing Set: | Architectural / Structural / Civil drawings dated April 18, 2026 (100% DD set)
Specifications: | Project Manual, Division 01–33 specifications (Rev. 3, April 2026)
Geotechnical Report: | Terracon Consultants, Inc., dated January 15, 2026
Site Survey: | Bowman Consulting Group, dated December 8, 2025
RFP / Program Brief: | Owner's program requirements v2.1, dated November 20, 2025
BIM Models: | Architectural and Structural Revit models, LOD 350
2. KEY ASSUMPTIONS
A.1 | Pricing reflects market conditions as of the estimate date. Escalation to the construction midpoint is applied at 3.5%/yr in the Construction Budget (cell H7); further market shifts tracked separately.
A.2 | Construction sequencing assumes no major site access constraints or owner-imposed work hour restrictions.
A.3 | Subcontractor market is assumed to be reasonably competitive (≥3 qualified bidders per major package).
A.4 | Prevailing wage rates apply per project location; non-union labor where market permits.
A.5 | Soils assumed suitable for standard spread footings per geotech report; no extensive soil remediation included.
A.6 | Utilities (power, water, fiber) are available at the property line; service entrance work included.
A.7 | Permits and AHJ approvals proceed on a normal review cycle; no expedited fees included.
A.8 | Owner-furnished IT equipment (servers, network gear) is excluded; OFCI integration coordination included.
A.9 | Single mobilization per building; phased delivery sequencing per program schedule.
A.10 | Labor productivity reflects regional norms; no premium time included in base estimate.
A.11 | Design basis: 90 MW total IT load across 800K SF gross; resiliency Tier III, redundancy N+1, rack density High (15–30 kW).
A.12 | Cooling design basis: Liquid-Cooled (DLC); Division 23 air / chilled-water / liquid scope scales from the active cooling preset on the Scenario & Presets tab.
A.13 | Location basis: pricing indexed to Northern Virginia at a location factor of 1.00 relative to the Northern Virginia baseline; set on the Location Factors tab and applied in the Construction Budget.
3. INCLUSIONS
I.1 | All civil work within property line: site clearing, mass excavation, structural fill, paving, fencing, security perimeter.
I.2 | Building envelope: foundations, structural steel, slabs, exterior wall systems, roofing, openings.
I.3 | MEP systems sized for stated IT load and Tier rating: utility service, generators, UPS, distribution, cooling, controls.
I.4 | Fire / life safety: clean agent suppression in data halls, pre-action sprinklers, VESDA detection, fire alarm, mass notification.
I.5 | Interior finishes: raised access flooring, gypsum partitions, painting, sealed concrete in support areas.
I.6 | Commissioning Levels 1–5 per ASHRAE / Uptime guideline.
I.7 | General conditions, contractor overhead and profit, and design contingency at the rate shown in Construction Budget cell C7.
I.8 | Permits, fees, builder's risk insurance, performance and payment bonds.
I.9 | Electronic security systems: access control, CCTV / video surveillance, intrusion detection, and visitor management across site perimeter, building, and data-hall white space.
I.10 | Structured cabling backbone (OS2 fiber + Cat6A trunks to MDA / IDA) and integrated controls — BMS, DCIM, and electrical power monitoring (EPMS).
3.1 GENERAL CONTRACTOR BASE SCOPE — TRADES (CSI DIVISIONS)
CSI | Trade / CSI Division — GC Base Scope |  |  | Status | Base Cost ($)
1 | General Conditions & Project Requirements |  |  | Included | 42983030.6039
Cx | Commissioning & Testing (Levels 1–5) |  |  | Included | 47367292.5
3 | Concrete |  |  | Included | 33466040.3876
4 | Masonry |  |  | Included | 5656068
5 | Metals / Structural Steel |  |  | Included | 40836399.762
6 | Wood, Plastics & Composites |  |  | Included | 1233678.6
7 | Thermal & Moisture Protection |  |  | Included | 38165650.875
8 | Openings (Doors, Frames & Glazing) |  |  | Included | 13742209.9774
9 | Finishes |  |  | Included | 33189552
10 | Specialties |  |  | Included | 4010233.425
11 | Equipment |  |  | Included | 1525590
12 | Furnishings |  |  | Included | 1217056.5
14 | Conveying Equipment (Elevators) |  |  | Included | 4104292.5
21 | Fire Suppression |  |  | Included | 22577593.5
22 | Plumbing |  |  | Included | 22312498.5188
23 | HVAC / Cooling Systems |  |  | Included | 226484248.0019
25 | Integrated Automation (BMS / DCIM / EPMS) |  |  | Included | 13470732
26 | Electrical / Critical Power |  |  | Included | 248147784.9504
27 | Communications / IT Infrastructure |  |  | Included | 60417387.7013
28 | Electronic Safety & Security |  |  | Included | 15750753.425
31 | Earthwork |  |  | Included | 25614732
32 | Exterior Improvements |  |  | Included | 9371809.4642
33 | Utilities |  |  | Included | 63598602.375
| GC BASE CONSTRUCTION COST (Div 01–33, incl. Commissioning) |  |  |  | 975243237.0674
All trades carried by the General Contractor are linked live to division subtotals on the Construction Budget. CSI divisions with no discrete scope on this greenfield project — Div 02 Existing Conditions and Div 13 Special Construction (containment carried within Specialties) — are captured within adjacent divisions. Soft costs, owner's contingency and OFCI IT equipment are excluded (see Exclusions).
4. EXCLUSIONS
E.1 | Land acquisition, due diligence, environmental remediation of pre-existing contamination.
E.2 | Off-site utility extensions beyond the property line (utility company scope).
E.3 | IT equipment: servers, switches, racks (when OFCI), structured cabling end-of-row terminations beyond Cat6A trunks.
E.4 | Owner's project management staff, owner's representative, legal fees.
E.5 | Move-in / commissioning of owner-furnished equipment.
E.6 | Operational costs, spare parts inventory, post-occupancy maintenance.
E.7 | Sales tax (assumed exempt or capitalized separately per owner accounting).
E.8 | Market escalation beyond the 3.5%/yr already applied to the construction midpoint (additional inflation or supply-chain shocks carried at owner level).
E.9 | Owner's contingency (carried at owner level, not in this estimate).
E.10 | Force majeure events; abnormal weather; pandemic-related labor or supply chain shocks.
E.11 | Construction financing and interest during construction (IDC); carried at owner level on the Total Development Cost tab.
E.12 | Utility capacity / demand charges, standby and interconnection fees, and utility-imposed substation contributions beyond the service entrance.
5. RISKS & SENSITIVITIES
# | Risk Description | Likelihood | Impact ($) | Mitigation | Owner
R-01 | Switchgear lead times exceed schedule float | High | Schedule slip + premium | Early procurement; alternate manufacturer pre-qualification | PM/Procurement
R-02 | Generator supply constraint due to global demand | High | $2M–$5M premium | Lock pricing 12+ months ahead; reserve mfg slots | Procurement
R-03 | Soil conditions worse than geotech indicates | Med | $500K–$2M | Allowance carried; over-excavation contingency | Civil/Estimating
R-04 | Concrete material price escalation | Med | ±5–10% on Div 03 | Lock pricing at GMP; monitor PPI | Estimating
R-05 | Labor availability in selected market | Med | Schedule + premium time | Pre-qualify multiple GCs; out-of-area labor plan | PM
R-06 | Permit / AHJ delays | Low–Med | Schedule slip | Early entitlement engagement; expediter on retainer | PM
R-07 | Design changes during DD/CD | Med | ±3–7% per change cycle | Tight change-control process; gated milestone reviews | Design Mgr
R-08 | Tariffs / trade policy on imported equipment | Med | ±2–5% on MEP | Domestic-source alternate priced; sensitivity tracked | Procurement
R-09 | Utility power interconnection capacity / energization timing | High | Schedule-critical; multi-month slip | Early utility engagement; reserve capacity; on-site generation bridging plan | Owner / PM
R-10 | Liquid-cooling (DLC) supply chain & technology maturity | Med | ±3–6% on Div 23; schedule | Pre-qualify CDU / coolant vendors; retain air+liquid hybrid flexibility | MEP / Procurement
6. SIGN-OFF
Role |  | Name | Signature | Date
Project Director
Client Acceptance
SCENARIO CONTROLS & VALUE ENGINEERING
Pricing Tier (Low/Mid/High) and Cooling Technology are driven from the 'Scenario & Presets' tab; defaults (Mid / Hybrid As-Designed) reproduce this estimate.
Cooling presets scale Division 23 air / chilled-water / liquid scope; Tier, Redundancy and Rack Density are documented configuration with an expected $/MW band by archetype.
Value-engineering options are logged on the 'Value Engineering' tab; items marked Accepted flow into the VE-Adjusted Total. VE and presets are illustrative pending MEP design confirmation.
Cooling topology (O-1, resolved): committed to an air + liquid hybrid via 'Scenario & Presets' → Cooling = Liquid-Cooled (DLC). In-Row air cooling now scales by the air-side factor (40%) and direct-liquid infrastructure + CDUs are engaged, replacing the prior stacked full-air + full-liquid scope. Division 23 −$33M; project total $1,122.7M → $1,088.3M. Revert by setting Cooling = Chilled Water (Air-Cooled).
MEP cost mix (O-2, resolved): Division 26 (Electrical, $248M) reviewed line-by-line — coherent critical-power scope (UPS, generators, PDU, busway, switchgear), no double-counts. The elevated MEP weight was driven by In-Row air cooling, not electrical; after the hybrid rationalization Electrical + HVAC ≈ 44% of cost, within the 45–55% norm.
Note on B6: Kevin: Enter cost manager / estimating firm name here. Drives the Prepared By and Reviewed By fields below.

## Benchmark Library
0.0175
Anchor each new estimate against this library. Filter by Tier, region, and vintage. Apply location and time-value adjustments before comparison.
Filter by Tier: | All | Filtered Median $/MW: | 1430000 | Filtered Count: | 10
# | Project | Region | Vintage | Tier | Buildings | GBA (SF) | IT Load (MW) | CSA $/SF | CSA $/MW | Total $/SF | Total $/MW | Total $/W | Notes
1 | Hyperscale Campus — NoVA Phase 2 | Northern Virginia | 2023 | Tier III | 4 | 1200000 | 96 | 220 | 1450000 | 880 | 11500000 | 11.5 | Greenfield, water-cooled chillers
2 | Edge Campus — Hillsboro | Hillsboro, OR | 2024 | Tier III | 2 | 480000 | 36 | 240 | 1620000 | 920 | 12200000 | 12.2 | Indirect evap cooling, lithium UPS
3 | Build-to-Suit — Phoenix | Phoenix, AZ | 2022 | Tier III+ | 3 | 850000 | 72 | 205 | 1380000 | 850 | 11000000 | 11 | Adiabatic; high ambient design
4 | Hyperscale — Quincy | Quincy, WA | 2023 | Tier II | 6 | 1800000 | 144 | 195 | 1310000 | 780 | 10200000 | 10.2 | Direct outside air economization
5 | Colocation Expansion — Ashburn | Ashburn, VA | 2024 | Tier IV | 1 | 280000 | 24 | 280 | 1900000 | 1080 | 14500000 | 14.5 | Brownfield, 2N redundant
6 | Hyperscale Campus — Dallas | Dallas-Fort Worth, TX | 2024 | Tier III | 5 | 1450000 | 120 | 215 | 1410000 | 870 | 11300000 | 11.3 | Liquid-cooling-ready
7 | Build-to-Suit — Council Bluffs | Council Bluffs, IA | 2022 | Tier III | 2 | 620000 | 48 | 185 | 1240000 | 760 | 9800000 | 9.8 | Air-cooled chillers, low-cost market
8 | Hyperscale — Santa Clara | Santa Clara, CA | 2023 | Tier III | 1 | 220000 | 18 | 340 | 2280000 | 1310 | 17800000 | 17.8 | Seismic + high cost market
9 | Edge Campus — Atlanta | Atlanta, GA | 2023 | Tier III | 3 | 720000 | 60 | 205 | 1380000 | 840 | 10900000 | 10.9 | Standard scope
10 | Hyperscale — Reno | Reno-Sparks, NV | 2024 | Tier III+ | 4 | 1100000 | 96 | 225 | 1510000 | 900 | 11700000 | 11.7 | DLC-ready, GPU buildout
BENCHMARK STATISTICS (across all projects above)
Statistic | [7 empty] | CSA $/SF | CSA $/MW | Total $/SF | Total $/MW | Total $/W
Min | [7 empty] | 185 | 1240000 | 760 | 9800000 | 9.8
Median | [7 empty] | 217.5 | 1430000 | 875 | 11400000 | 11.4
Mean | [7 empty] | 231 | 1548000 | 919 | 12090000 | 12.09
Max | [7 empty] | 340 | 2280000 | 1310 | 17800000 | 17.8
CURRENT ESTIMATE vs BENCHMARK MEDIAN
Current Estimate | [7 empty] | 0 | 0 | 1360.4273 | 12092686.9674 | 12.0927
Benchmark Median | [7 empty] | 217.5 | 1430000 | 875 | 11400000 | 11.4
Δ vs Median | [7 empty] | -217.5 | -1430000 | 485.4273 | 692686.9674 | 0.69269
Δ % | [7 empty] | -100% | -100% | 55.48% | 6.076% | 6.076%
STAKEHOLDER BENCHMARKS — RETURNS, CAPITAL EFFICIENCY & CREDIT
Typical institutional ranges for Tier III hyperscale / wholesale data centers; current figures link live from the model (TDC, Pro Forma, Capital Stack). Illustrative — calibrate Low/Median/High to deal-specific quotes.
| Metric |  |  |  | Market Low | Median | High | Current Project |  | Position vs Market
◆ DEVELOPER — COST & DELIVERY
| All-in development cost ($/MW) |  |  |  | 13000000 | 16000000 | 22000000 | 16809708.6701 |  | ● In market range
| Construction (hard) cost ($/MW) |  |  |  | 9800000 | 11400000 | 17800000 | 12092686.9674 |  | ● In market range
| Hard cost (% of all-in TDC) |  |  |  | 65% | 72% | 80% | 71.94% |  | ● In market range
| Design PUE |  |  |  | 1.2 | 1.4 | 1.6 | 1.4 |  | ● In market range
| Schedule to energization (months) |  |  |  | 18 | 24 | 36 | 30 |  | ● In market range
◆ CFO — CAPITAL EFFICIENCY
| Soft + financing + contingency (% of TDC) |  |  |  | 20% | 28% | 35% | 28.06% |  | ● In market range
| Owner's contingency (%) |  |  |  | 5% | 8% | 12% | 5% |  | ● In market range
| Interest during construction (% of TDC) |  |  |  | 3% | 4.5% | 7% | 5.549% |  | ● In market range
| All-in cost ($/SF) |  |  |  | 1500 | 1870 | 2400 | 1891.0922 |  | ● In market range
◆ INVESTOR — RETURNS
| Stabilized yield-on-cost |  |  |  | 8% | 10% | 13% | 10.9% |  | ● In market range
| Going-in yield (Yr-1 NOI ÷ TDC) |  |  |  | 4.5% | 5.5% | 7% | 5.065% |  | ● In market range
| Exit / terminal cap rate |  |  |  | 5.5% | 6.5% | 7.5% | 6.5% |  | ● In market range
| Lease rate ($/kW IT / month) |  |  |  | 120 | 150 | 190 | 165 |  | ● In market range
| Unlevered IRR (8-yr hold) |  |  |  | 9% | 12% | 16% | 17.44% |  | ▲ Above market
| Levered equity IRR |  |  |  | 14% | 18% | 25% | 26.65% |  | ▲ Above market
| Levered equity multiple (8-yr) |  |  |  | 1.8 | 2.2 | 3 | 5.1974 |  | ▲ Above market
| Development margin (% of cost) |  |  |  | 15% | 25% | 40% | 67.71% |  | ▲ Above market
◆ LENDER — CREDIT & FINANCEABILITY
| Loan-to-cost (LTC) |  |  |  | 50% | 60% | 70% | 60% |  | ● In market range
| Stabilized DSCR |  |  |  | 1.25 | 1.4 | 1.75 | 2.3726 |  | ▲ Above market
| Debt yield (stabilized) |  |  |  | 8.5% | 10% | 12% | 18.17% |  | ▲ Above market
| All-in permanent loan rate |  |  |  | 5.5% | 6.5% | 8% | 6.5% |  | ● In market range
| Sponsor equity (% of cost) |  |  |  | 30% | 40% | 50% | 40% |  | ● In market range
STAKEHOLDER POSITIONING SUMMARY
| Stakeholder |  |  |  | In Range | Above Mkt | Below Mkt | Metrics |  | Read
| Developer — Cost & Delivery |  |  |  | 5 | 0 | 0 | 5 |  | Cost position: at or below market
| CFO — Capital Efficiency |  |  |  | 4 | 0 | 0 | 4 |  | Capital efficiency: within norms
| Investor — Returns |  |  |  | 4 | 4 | 0 | 8 |  | Returns: exceed market benchmarks
| Lender — Credit & Financeability |  |  |  | 3 | 2 | 0 | 5 |  | Credit: coverage stronger than market

## Power & Space Capacity
POWER & SPACE CAPACITY MODEL
Ties cost to engineering: IT load → electrical / cooling / space sizing, the binding constraint, and stranded capacity. Yellow cells are inputs.
1 · DESIGN INPUTS & REFERENCES
IT load (design) | 90 | MW — from Campus Rollup
Gross building area (GBA) | 800000 | SF — from Campus Rollup
PUE (design) | 1.3 | facility kW per IT kW
Average utilisation | 80% | of IT capacity, annualised
Rack power density | 20 | kW per rack
Area per rack (incl. aisles) | 30 | SF per rack
Redundancy (from preset) | N+1 | N / N+1 / 2N / 2N+1
Redundancy de-rate factor | 1.2 | usable = provisioned ÷ factor
Facility load | 117 | MW = IT × PUE
2 · CAPACITY BALANCE (provisioned → supportable IT)
Subsystem | Provisioned | Unit | Supportable IT (MW) | Stranded (MW)
UPS / critical power | 108 | MW | 90 | 0.25641
Standby generation | 140 | MW | 89.7436 | 0
Cooling plant | 31000 | tons | 90.8558 | 1.1122
Utility / transformers | 130 | MW | 100 | 10.2564
Design IT load (target): | 90
Usable IT (binding subsystem): | 89.7436
Binding constraint: | Standby generation
Capacity adequacy: | ▲ Short by 0.3 MW — relieve binding subsystem
3 · SPACE PROGRAM
Rack count (capacity) | 4500 | racks = IT kW ÷ density
White-space area | 135000 | SF = racks × area/rack
White space per MW | 1500 | SF / MW
White space as % of GBA | 16.88% | of gross building area
Support / MEP / admin balance | 665000 | SF (GBA − white space)
4 · UNIT COST METRICS (from the live estimate)
Cost per MW (IT) | 12092686.9674 | per IT MW
Cost per MW (facility) | 9302066.898 | per facility MW
Cost per rack | 241853.7393 | per rack position
Cost per cooling ton | 35107.8009 | per installed ton
Cost per SF | 1360.4273 | per gross SF
Cost per IT watt | 12.0927 | per IT watt
(lookup — do not edit)
Redundancy | Factor
N | 1
N+1 | 1.2
2N | 2
2N+1 | 2.1
5 · STAKEHOLDER VIEW — CAPACITY TRANSLATED FOR CAPITAL PARTNERS
Translates the engineering capacity above into the metric each capital partner underwrites. Links live to the estimate, TDC, and Pro Forma lease rate.
◆ DEVELOPER — DELIVERABLE CAPACITY
Usable IT capacity (binding) | 89.7436 | limited by standby generation
Capacity adequacy vs design | 99.72% | usable ÷ design IT target
Stranded provisioned capacity | 10.2564 | MW provisioned beyond binding (relievable)
◆ CFO — CAPITAL EFFICIENCY
All-in cost per usable MW | 16857736.4091 | TDC ÷ usable IT MW
Construction cost per usable MW | 12127237.5016 | hard construction ÷ usable IT MW
Capacity efficiency | 99.72% | usable ÷ design (capital utilisation)
◆ INVESTOR — REVENUE CAPACITY
Leasable IT capacity | 89.7436 | revenue-generating IT (usable)
Gross revenue capacity @ lease rate | 177692307.6923 | $/yr at full lease ($165/kW/mo)
Revenue at risk — binding shortfall | 507692.3077 | $/yr forgone vs design IT
◆ LENDER — CAPACITY SECURITY
Redundancy level | N+1 | N / N+1 / 2N resiliency tier
Capacity adequacy | ▲ Short 0.3 MW | provisioned vs design IT load
Design utilisation (load factor) | 80% | of IT capacity, annualised

## Bid Cover Sheet
SEALED BID
DO NOT OPEN UNTIL PUBLIC BID OPENING
Data Center Template, Northern Virginia
Hyperscale Data Center ¦ Loudoun County, VA
SOLICITATION
Solicitation / RFP No.:
Bid Due Date & Time:
Delivery Method: | CM-at-Risk / Guaranteed Maximum Price (GMP)
SUBMIT TO
Owner / Procurement: | Owner Program Management Office (edit)
Attention: | Attn: Procurement & Contracts
Address: | [ Insert delivery address, room / desk ]
FROM (BIDDER)
Company:
Contact / Phone:
SEALING & LABELING INSTRUCTIONS
1. Enclose the completed, signed Bid Form and all required attachments in a sealed, opaque envelope or package.
2. Affix this cover sheet to the outside of the sealed package.
3. Mark the package “SEALED BID — DO NOT OPEN” and deliver to the Submit-To address before the Bid Due Date & Time.
4. Late submissions will not be accepted. Faxed or emailed bids are not accepted unless expressly permitted in the solicitation.
Do not write the bid amount anywhere on this cover. The Owner is not responsible for premature opening of bids not properly sealed and labeled.
REQUIRED DOCUMENTS — CONFIRM ENCLOSED
☐ Completed & signed Bid Form (every division priced or excluded)
☐ Bid bond / bid security (amount per solicitation)
☐ Certificate of Insurance meeting Owner requirements
☐ Contractor's license & statement of qualifications
☐ Proposed project schedule (to Substantial Completion)
☐ List of major subcontractors by division
☐ Audited financial statement / surety bonding letter
☐ Signed acknowledgement of all addenda
☐ Safety record (EMR) & three comparable project references

## GC Bid Form
GENERAL CONTRACTOR BID FORM
Data Center Template, Northern Virginia — Hyperscale Data Center
CONFIDENTIAL — Submit a sealed, signed bid by the Bid Due Date stated below. All amounts in US$.
1 · PROJECT & SOLICITATION
Project: |  | Data Center Template, Northern Virginia
Location: |  | Loudoun County, VA
Owner / Client: |  | Confidential Hyperscaler
Delivery Method: |  | CM-at-Risk / Guaranteed Maximum Price (GMP)
RFP / Solicitation No.:
Bid Due Date:
Target NTP (ref): |  | 2026-05-01
Target Completion (ref): |  | Q1 2029
2 · BIDDER INFORMATION
Company Name:
Primary Contact / Title:
Address:
Phone / Email:
Contractor License No.:
Bonding Capacity / Surety:
Date Submitted:
3 · BASE BID BY TRADE / DIVISION (CSI)
Enter a lump-sum base bid for each division below. Leave blank only if excluding a division — note all exclusions in §7.
# | Trade / Division (CSI) | Base Bid (US$) | Notes / Clarifications
1 | General Conditions & Requirements
2 | Commissioning & Testing
3 | Div 03 — Concrete
4 | Div 04 — Masonry
5 | Div 05 — Metals / Structural Steel
6 | Div 06 — Wood, Plastics & Composites
7 | Div 07 — Thermal & Moisture Protection
8 | Div 08 — Openings
9 | Div 09 — Finishes
10 | Div 10 — Specialties
11 | Div 11 — Equipment
12 | Div 12 — Furnishings
13 | Div 14 — Conveying Equipment
14 | Div 21 — Fire Suppression
15 | Div 22 — Plumbing
16 | Div 23 — HVAC / Cooling Systems
17 | Div 25 — Integrated Automation
18 | Div 26 — Electrical / Critical Power
19 | Div 27 — Communications / IT Infrastructure
20 | Div 28 — Electronic Safety & Security
21 | Div 31 — Earthwork
22 | Div 32 — Exterior Improvements
23 | Div 33 — Utilities
24 | Soft Costs / Pre-Construction
| TOTAL BASE BID (sum of all divisions) | 0
4 · ALTERNATES (ADD / DEDUCT)
# | Alternate Description | Add / (Deduct) $ | Notes
1 | Upgrade to N+2 redundancy on critical cooling
2 | Add 10 MW incremental UPS capacity
3 | Premium to accelerate Substantial Completion by 2 months
4 | Substitute air-cooled chillers for water-cooled plant
5 | Bidder-proposed alternate (describe):
5 · UNIT PRICES (FOR CHANGES IN SCOPE)
# | Item | Unit | Unit Price (US$)
1 | Structural concrete — placed & finished | CY
2 | Reinforcing steel — installed | TON
3 | Mass excavation | CY
4 | Select structural fill — imported & compacted | CY
5 | Branch conduit & wire (typical run) | LF
6 · SCHEDULE COMMITMENT
Proposed mobilization (days from NTP):
Proposed Substantial Completion date:
Total duration (calendar months):
Can you meet the Owner's Target Completion? (Y/N):
Schedule comments:
7 · QUALIFICATIONS, ASSUMPTIONS & EXCLUSIONS
List all qualifications, assumptions, and scope exclusions below. Any division left blank in §3 must be noted here as excluded. Attach additional sheets as needed.
8 · ACKNOWLEDGEMENTS
Addenda received (list numbers):
Bid bond / security attached (Y/N):
Bid valid for (calendar days):
Insurance meets Owner requirements (Y/N):
9 · CERTIFICATION & SIGNATURE
The undersigned certifies this bid is genuine, made without collusion, complies with the solicitation and all addenda, and that the signer is authorized to bind the bidder.
Authorized Signature:
Printed Name / Title:
Company:
Date:
Company Seal:

## Bid Leveling
BID LEVELING — GENERAL CONTRACTOR ANALYSIS
Trade-by-trade comparison of general contractor bids vs. the engineer's estimate. Baseline = Construction Budget. Enter GC bids in the blue input cells.
EXECUTIVE SUMMARY
RECOMMENDED GC |  | AWARD VALUE |  | SAVINGS vs EE |  | ENGINEER'S ESTIMATE |  | GC BIDS RECEIVED
— enter bids |  | 0 |  | 0 |  | 1088341827.0674 |  | 0
TRADE-BY-TRADE GC BID COMPARISON
# | Trade / Division (CSI) | Engineer's Estimate | National Build Group | Western Constructors | Metro Mission Critical | Pinnacle CM (DC specialist) | Low Bid | Δ Low vs EE | Notes
1 | General Conditions & Requirements | 42983030.6039
2 | Commissioning & Testing | 47367292.5
3 | Div 03 — Concrete | 33466040.3876
4 | Div 04 — Masonry | 5656068
5 | Div 05 — Metals / Structural Steel | 40836399.762
6 | Div 06 — Wood, Plastics & Composites | 1233678.6
7 | Div 07 — Thermal & Moisture Protection | 38165650.875
8 | Div 08 — Openings | 13742209.9774
9 | Div 09 — Finishes | 33189552
10 | Div 10 — Specialties | 4010233.425
11 | Div 11 — Equipment | 1525590
12 | Div 12 — Furnishings | 1217056.5
13 | Div 14 — Conveying Equipment | 4104292.5
14 | Div 21 — Fire Suppression | 22577593.5
15 | Div 22 — Plumbing | 22312498.5188
16 | Div 23 — HVAC / Cooling Systems | 226484248.0019
17 | Div 25 — Integrated Automation | 13470732
18 | Div 26 — Electrical / Critical Power | 248147784.9504
19 | Div 27 — Communications / IT Infrastructure | 60417387.7013
20 | Div 28 — Electronic Safety & Security | 15750753.425
21 | Div 31 — Earthwork | 25614732
22 | Div 32 — Exterior Improvements | 9371809.4642
23 | Div 33 — Utilities | 63598602.375
24 | Soft Costs / Pre-Construction | 113098590
| TOTAL — ALL TRADES | 1088341827.0674 | 0 | 0 | 0 | 0 | 0
GC BID SUMMARY & RECOMMENDATION | ▲ Columns D–G link live to the GC Bid Form. Currently mapped to: (no bidder selected)
| Workflow: select the bidder on the GC Bid Form, enter their division prices, then Copy → Paste-Values that column here to retain it before processing the next bidder. | Total Bid | Δ vs EE ($) | Δ vs EE (%) | Rank | Status / Qualification
| National Build Group | 0 |  |  | —
| Western Constructors | 0 |  |  | —
| Metro Mission Critical | 0 |  |  | —
| Pinnacle CM (DC specialist) | 0 |  |  | —
| RECOMMENDATION | Enter GC bids in the blue cells to generate a recommendation.

## Bid Evaluation
BID EVALUATION — WEIGHTED SCORING
CMAR / GMP selection. Yellow = inputs (weights, GMP, qualitative scores 1–10). Price score is auto-normalised (lowest bid = 10). Complements the price-only Bid Leveling tab.
Package: | General Contractor / CMAR — Data Center Template, NoVA
1 · EVALUATION CRITERIA & WEIGHTS
|  | Criterion → | Price | Schedule | Technical | Experience | Safety (EMR) | Financial
| Weights (must total 100%): |  | 40% | 15% | 15% | 15% | 10% | 5% | 100% | ✓
2 · BIDDER SCORING (qualitative scores 1–10) | [10 empty] | WEIGHTED CONTRIBUTION BY CRITERION
# | Bidder (CM) | GMP Bid | Price Score | Sched. | Tech. | Exp. | Safety | Fin. | Weighted Score | Rank | Bidder | Price | Schedule | Technical | Experience | Safety | Financial
1 | National Build Group | 1640000000 | 9.66 | 8 | 9 | 9 | 8 | 9 | 9.014 | 2 | National | 3.864 | 1.2 | 1.35 | 1.35 | 0.8 | 0.45
2 | Western Constructors | 1585000000 | 10 | 7 | 7 | 8 | 9 | 7 | 8.55 | 4 | Western | 4 | 1.05 | 1.05 | 1.2 | 0.9 | 0.35
3 | Metro Mission Critical | 1612000000 | 9.83 | 9 | 8 | 7 | 7 | 8 | 8.632 | 3 | Metro Mi | 3.932 | 1.35 | 1.2 | 1.05 | 0.7 | 0.4
4 | Pinnacle CM (DC specialist) | 1675000000 | 9.46 | 8 | 9 | 10 | 9 | 10 | 9.234 | 1 | Pinnacle | 3.784 | 1.2 | 1.35 | 1.5 | 0.9 | 0.5
3 · RECOMMENDATION
Recommended award: |  | Pinnacle CM (DC specialist)
Winning weighted score: |  | 9.234
Their GMP vs low bid: |  | $90M above lowest bid (quality-justified premium)
4 · GMP VARIANCE ANALYSIS
# | General Contractor | GMP Bid | Leveled Constr. (Bid Leveling) | Implied GC Fee / Soft | vs Low GMP ($) | vs Low GMP (%) | vs Avg GMP (%) | vs Trades EE (%) | Price Rank
1 | National Build Group | 1640000000 | 0 | — | 55000000 | 3.47% | 0.7371% | 68.16% | 3
2 | Western Constructors | 1585000000 | 0 | — | 0 | 0% | -2.641% | 62.52% | 1
3 | Metro Mission Critical | 1612000000 | 0 | — | 27000000 | 1.703% | -0.9828% | 65.29% | 2
4 | Pinnacle CM (DC specialist) | 1675000000 | 0 | — | 90000000 | 5.678% | 2.887% | 71.75% | 4
| Low GMP | 1585000000
| Average GMP | 1628000000
| High GMP | 1675000000
| Spread (High − Low) | 90000000 | 5.678%
| Engineer's Estimate (Trades, excl. Soft Costs) | 975243237.0674
Leveled Constr. and Implied GC Fee populate from Bid Leveling once GC trade bids are entered. 'vs Trades EE' compares each GMP to the construction-trades estimate (excl. owner soft costs, $975M).
5 · TRADE-BY-TRADE BID DETAIL — GC-BID TRADES (EXCL. SOFT COSTS)
| Trade / Division | Eng. Estimate | National Build Group | Western Constructors | Metro Mission Critical | Pinnacle CM (DC specialist) | Low Bid | Δ vs EE
| General Conditions & Requirements | 42983030.6039
| Commissioning & Testing | 47367292.5
| Div 03 — Concrete | 33466040.3876
| Div 04 — Masonry | 5656068
| Div 05 — Metals / Structural Steel | 40836399.762
| Div 06 — Wood, Plastics & Composites | 1233678.6
| Div 07 — Thermal & Moisture Protection | 38165650.875
| Div 08 — Openings | 13742209.9774
| Div 09 — Finishes | 33189552
| Div 10 — Specialties | 4010233.425
| Div 11 — Equipment | 1525590
| Div 12 — Furnishings | 1217056.5
| Div 14 — Conveying Equipment | 4104292.5
| Div 21 — Fire Suppression | 22577593.5
| Div 22 — Plumbing | 22312498.5188
| Div 23 — HVAC / Cooling Systems | 226484248.0019
| Div 25 — Integrated Automation | 13470732
| Div 26 — Electrical / Critical Power | 248147784.9504
| Div 27 — Communications / IT Infrastructure | 60417387.7013
| Div 28 — Electronic Safety & Security | 15750753.425
| Div 31 — Earthwork | 25614732
| Div 32 — Exterior Improvements | 9371809.4642
| Div 33 — Utilities | 63598602.375
| TOTAL — GC-BID TRADES (EXCL. SOFT COSTS) | 975243237.0674 | 0 | 0 | 0 | 0 | 0
6 · GENERAL CONTRACTOR QUALIFICATIONS & DUE DILIGENCE
Firm qualifications captured per bidding GC — complete during due diligence. Any "Fail" on a mandatory gate (bottom row) disqualifies regardless of weighted score.
| Qualification / Attribute | Min Requirement | National Build Group | Western Constructors | Metro Mission Critical | Pinnacle CM (DC specialist)
Firm HQ / local office presence
Years in business
Annual revenue ($M)
Bonding capacity — aggregate ($M)
Surety & bond rating
Current backlog ($M)
Data-center projects completed (#)
DC capacity delivered (MW)
Self-perform capability (% of work)
Safety EMR (3-yr avg)
Key project executive / PM assigned
Mandatory gate — insurance, licensing & bonding

## Procurement & Long-Lead
PROCUREMENT & LONG-LEAD TRACKER
Order-By = Required-On-Site − (lead + buffer). Long leads on transformers, gear and generators mean several packages must be ordered before mobilization.
1 · STATUS PARAMETERS
Data Date: | 2026-07-01
Project Start (ref): | 2026-05-01
Annual escalation (ref): | 3.5%
2 · LONG-LEAD EQUIPMENT REGISTER
Equipment Package | Div | Supply Responsibility | Budget | Lead (wks) | Buffer (wks) | Required On-Site | Order-By Date | Days to Order-By | Escal. Exposure | Status | Procurement Flag | Typical OEM / Vendor Pool | Installed By | Deposit % | Deposit Due | Supply-Chain Risk
Structural Steel | 5 | GC-Supplied | 35000000 | 22 | 4 | 2026-12-01 | 2026-06-02 | -29 | 518269.2308 | PO Released | ✓ Ordered | Mill + AISC fabricator (bid) | GC self-perform / steel erector | 15% | 5250000 | Med — mill rolling + fab capacity
Raised Access Floor & Aisle Containment | 9 | GC-Supplied | 21000000 | 18 | 4 | 2027-11-01 | 2027-05-31 | 334 | 254423.0769 | Not Started | On track | Tate / ASM / Polargy / Subzero | GC self-perform — floor & containment | 20% | 4200000 | Low — stock product
Clean-Agent / Pre-Action Fire Suppression | 21 | Owner (OFCI) | 15000000 | 24 | 4 | 2027-11-29 | 2027-05-17 | 320 | 242307.6923 | Not Started | On track | Fike / Kidde / Victaulic / Viking | Fire-protection sub — pipe, cylinders, detection | 15% | 2250000 | Low — domestic supply
CRAH / In-Row Cooling Units | 23 | Owner (OFCI) | 60000000 | 28 | 4 | 2028-01-01 | 2027-05-22 | 325 | 1130769.2308 | Not Started | On track | Vertiv / Stulz / Schneider / Trane | Mechanical sub — floor set & pipe | 20% | 12000000 | Med — coil + EC fan supply
Centrifugal Chillers | 23 | Owner (OFCI) | 50000000 | 45 | 6 | 2027-10-01 | 2026-10-09 | 100 | 1514423.0769 | Not Started | On track | Trane / Carrier / JCI / Daikin | Mechanical sub — rig & pipe; OEM startup | 30% | 15000000 | High — compressor + 45-wk lead
Direct Liquid Cooling / CDUs | 23 | Owner (OFCI) | 46000000 | 34 | 6 | 2028-02-01 | 2027-04-27 | 300 | 1052692.3077 | Not Started | On track | Vertiv / CoolIT / Motivair / Boyd | Mechanical/IT sub — manifold & CDU | 30% | 13800000 | High — emerging supply, few OEMs
Thermal Energy Storage | 23 | Owner (OFCI) | 43000000 | 30 | 6 | 2028-01-01 | 2027-04-24 | 297 | 868269.2308 | Not Started | On track | DN Tanks / CB&I / Trane TES | Civil/Mech sub — tank & glycol fill | 25% | 10750000 | Med — site-built tank schedule
Air-Cooled Chillers (N+1 backup) | 23 | Owner (OFCI) | 36000000 | 40 | 6 | 2027-11-01 | 2026-12-14 | 166 | 969230.7692 | Not Started | On track | Trane / Carrier / Daikin / JCI | Mechanical sub — yard rig & pipe | 30% | 10800000 | High — compressor + 40-wk lead
Air-Side Economizers / Evaporative Units | 23 | Owner (OFCI) | 24000000 | 32 | 6 | 2027-11-29 | 2027-03-08 | 250 | 516923.0769 | Not Started | On track | Munters / Nortek / Stulz | Mechanical sub — roof rig & duct | 25% | 6000000 | Med — engineered units
Air Handling Units (AHUs) | 23 | Owner (OFCI) | 20000000 | 30 | 4 | 2027-11-01 | 2027-03-08 | 250 | 403846.1538 | Not Started | On track | Daikin / Trane / Nailor / Temtrol | Mechanical sub — rig, duct & pipe | 20% | 4000000 | Med — coil & fan lead
Chilled-Water & Condenser Pumps / Skids | 23 | Owner (OFCI) | 16000000 | 28 | 4 | 2027-10-01 | 2027-02-19 | 233 | 301538.4615 | Not Started | On track | Bell & Gossett / Armstrong / Grundfos | Mechanical sub — skid set & align | 20% | 3200000 | Med — motor & VFD supply
Cooling Towers | 23 | Owner (OFCI) | 14000000 | 26 | 4 | 2027-11-01 | 2027-04-05 | 278 | 245000 | Not Started | On track | BAC / Evapco / SPX | Mechanical sub — roof/yard rig & pipe | 20% | 2800000 | Med — fabrication slot
Bulk Fuel Oil Storage Farm | 23 | Owner (OFCI) | 14000000 | 26 | 6 | 2027-06-03 | 2026-10-22 | 113 | 245000 | Not Started | On track | Highland / Modern Welding / Pryco | Civil/Mech sub — tank, pumps & piping | 20% | 2800000 | Med — containment + AHJ
Generator Fuel & Day Tanks | 23 | Owner (OFCI) | 12000000 | 20 | 4 | 2027-09-01 | 2027-03-17 | 259 | 161538.4615 | Not Started | On track | Pryco / Highland Tank / Modern Welding | Mechanical sub — set & pipe to gens | 20% | 2400000 | Low — domestic fab
EPMS / DCIM / BMS Controls | 25 | Owner (OFCI) | 26000000 | 30 | 6 | 2028-01-01 | 2027-04-24 | 297 | 525000 | Not Started | On track | Schneider EcoStruxure / ABB / Honeywell | Controls/LV sub — field devices & head-end | 20% | 5200000 | Med — chip content; integration
Diesel Generators (2.5 MW units) | 26 | Owner (OFCI) | 120000000 | 65 | 8 | 2027-08-01 | 2026-03-08 | -115 | 5250000 | Not Started | ● LATE — order now | Caterpillar / Cummins / MTU / Kohler | Mechanical sub — pad set, fuel/exhaust; OEM startup | 30% | 36000000 | High — engine allocation; Tier 4
Medium-Voltage Transformers (utility + unit subs) | 26 | Owner (OFCI) | 95000000 | 78 | 8 | 2027-09-01 | 2026-01-07 | -175 | 4987500 | RFQ Issued | ● LATE — order now | ABB / Siemens / Eaton / Virginia Trans. | Electrical sub — crane set on pad; OEM commissions | 30% | 28500000 | High — 78-wk lead; core/coil shortage
UPS Systems | 26 | Owner (OFCI) | 90000000 | 36 | 6 | 2027-11-01 | 2027-01-11 | 194 | 2180769.2308 | Not Started | On track | Vertiv / Schneider / ABB / Eaton | Electrical sub — set; OEM commissions | 25% | 22500000 | Med — module + battery lead
Medium-Voltage Switchgear | 26 | Owner (OFCI) | 68000000 | 60 | 6 | 2027-07-01 | 2026-03-26 | -97 | 2746153.8462 | RFQ Issued | ● LATE — order now | Eaton / Schneider / Siemens / Powell | Electrical sub — set, bus & terminate | 25% | 17000000 | High — gear lead 50-60 wk
PDUs / Remote Power Panels | 26 | Owner (OFCI) | 45000000 | 28 | 4 | 2028-01-01 | 2027-05-22 | 325 | 848076.9231 | Not Started | On track | Vertiv / Schneider / Server Technology | Electrical sub — floor set & whip | 20% | 9000000 | Med — copper + breaker supply
Battery Energy Storage System (BESS) | 26 | Owner (OFCI) | 40000000 | 40 | 8 | 2027-07-02 | 2026-07-31 | 30 | 1076923.0769 | Not Started | ▲ Order ≤30 days | Tesla / Fluence / Eaton / Saft | Electrical sub — pad set; OEM commissions | 30% | 12000000 | High — Li-ion cell allocation; AHJ
Generator Paralleling Switchgear | 26 | Owner (OFCI) | 38000000 | 52 | 6 | 2027-08-01 | 2026-06-21 | -10 | 1330000 | Not Started | ● LATE — order now | ASCO / Russelectric / Cummins | Electrical sub — integrate w/ gen plant | 25% | 9500000 | High — engineered-to-order controls
Busway Distribution | 26 | Owner (OFCI) | 32000000 | 22 | 4 | 2027-12-01 | 2027-06-02 | 336 | 473846.1538 | Not Started | On track | Starline / Universal Electric / Eaton | Electrical sub — overhead hang & section | 20% | 6400000 | Med — copper price volatility
Static Transfer Switches / ATS | 26 | Owner (OFCI) | 28000000 | 44 | 4 | 2027-10-01 | 2026-10-30 | 121 | 829230.7692 | Not Started | On track | ASCO / Cummins / Russelectric / Vertiv | Electrical sub — set & terminate | 20% | 5600000 | Med — semiconductor content
Low-Voltage Switchboards & Panelboards | 26 | Owner (OFCI) | 22000000 | 30 | 4 | 2027-06-02 | 2026-10-07 | 98 | 444230.7692 | Not Started | On track | Eaton / Schneider / Siemens / ABB | Electrical sub — set & feeder terminate | 20% | 4400000 | Med — panel/breaker backlog
Medium-Voltage Cable & Terminations | 26 | Owner (OFCI) | 18000000 | 32 | 4 | 2027-02-02 | 2026-05-26 | -36 | 387692.3077 | Not Started | ● LATE — order now | Southwire / Prysmian / Okonite | Electrical sub — pull, splice & terminate | 15% | 2700000 | Med — copper + reel lead
IT Server Racks & Cabinets | 27 | Owner (OFCI) | 30000000 | 20 | 4 | 2028-03-03 | 2027-09-17 | 443 | 403846.1538 | Not Started | On track | Vertiv / Eaton / Rittal / APC | Owner IT vendor; GC sets & levels | 20% | 6000000 | Med — volume + tariff exposure
Structured Cabling / Network Backbone | 27 | Owner (OFCI) | 18000000 | 18 | 4 | 2028-03-03 | 2027-10-01 | 457 | 218076.9231 | Not Started | On track | CommScope / Corning / Panduit / Belden | Low-voltage/cabling sub — pathway & terminations | 15% | 2700000 | Low — domestic distribution
Security System (Access Control & CCTV) | 28 | Owner (OFCI) | 11000000 | 22 | 4 | 2028-02-01 | 2027-08-03 | 398 | 162884.6154 | Not Started | On track | Genetec / Lenel / Avigilon / Axis | Low-voltage/security sub — devices & head-end | 15% | 1650000 | Low — broad supplier base
TOTAL — tracked long-lead value |  |  | 1087000000 | [5 empty] | 30288461.5385 | [5 empty] | 264400000
3 · PROCUREMENT SUMMARY
Tracked long-lead value | 1087000000
Packages past Order-By (LATE) | 5
Packages to order within 30 days | 1
Total escalation exposure | 30288461.5385
Earliest Order-By date | 2026-01-07
Owner-Supplied (OFCI) value | 1031000000
Owner-Supplied packages | 27
Owner-Supplied escalation exposure | 29515769.2308
GC-Supplied value | 56000000
Deposit cash due at PO (all) | 264400000
— OFCI deposit cash due | 254950000
— GC-Supplied deposit cash due | 9450000
High supply-chain-risk packages | 8
Formulas:
Order-By Date = [Required On-Site]-([Lead (wks)]+[Buffer (wks)])*7

## Construction Schedule
CONSTRUCTION SCHEDULE — CRADLE TO GRAVE (Site Selection → Site Opening)
MS-Project-style master schedule with CPM logic & procurement-driven delivery→install constraints. Durations (blue) are inputs; installs start at the LATER of their sequence predecessor or equipment delivery. Construction NTP is tied to Construction Budget!F3.
Site Selection Start: | 2025-01-01 |  |  | Phase |  | Critical task
Data Date: | 2026-07-01 |  |  | Task (float) |  | Milestone |  | Equip delivery
Construction Start (NTP): | 2026-05-01 | Sched. NTP / Mobilize: | 2026-05-01 | Tie? | ✓ Tied | Target Completion: | Q1 2029 | Scheduled Go-Live: | 2029-02-24 | Go-Live vs Target: | ✓ On/Before Q1 2029
WBS | Task / Activity | Trade / Crew | Dur (days) | Start | Finish | Baseline Finish | Var (d) | Pred | Float (d) | Critical? | % Comp | Status | Owner | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01 | 2025-07-01 | 2025-08-01 | 2025-09-01 | 2025-10-01 | 2025-11-01 | 2025-12-01 | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01 | 2026-09-01 | 2026-10-01 | 2026-11-01 | 2026-12-01 | 2027-01-01 | 2027-02-01 | 2027-03-01 | 2027-04-01 | 2027-05-01 | 2027-06-01 | 2027-07-01 | 2027-08-01 | 2027-09-01 | 2027-10-01 | 2027-11-01 | 2027-12-01 | 2028-01-01 | 2028-02-01 | 2028-03-01 | 2028-04-01 | 2028-05-01 | 2028-06-01 | 2028-07-01 | 2028-08-01 | 2028-09-01 | 2028-10-01 | 2028-11-01 | 2028-12-01 | 2029-01-01 | 2029-02-01 | 2029-03-01 | 2029-04-01 | 2029-05-01 | 2029-06-01 | 2029-07-01 | 2029-08-01 | 2029-09-01 | 2029-10-01 | 2029-11-01 | 2029-12-01
1 | Site Selection & Feasibility |  | 155 | 2025-01-01 | 2025-06-05 | 2025-06-05 | 0 |  |  |  | 100% | Complete | Developer
1.1 | Market & power availability study | Site selection | 45 | 2025-01-01 | 2025-02-15 | 2025-02-15 | 0 | — | 0 | ● CRITICAL | 100% | Complete | Developer
1.2 | Site identification & shortlisting | Site selection | 30 | 2025-02-15 | 2025-03-17 | 2025-03-17 | 0 | 1.1 | 0 | ● CRITICAL | 100% | Complete | Developer
1.3 | Geotechnical & environmental due diligence | Consultants | 60 | 2025-03-17 | 2025-05-16 | 2025-05-16 | 0 | 1.2 | 0 | ● CRITICAL | 100% | Complete | Owner
1.4 | Fatal-flaw & constructability review | CM / A-E | 20 | 2025-05-16 | 2025-06-05 | 2025-06-05 | 0 | 1.3 | 0 | ● CRITICAL | 100% | Complete | Owner / CM
1.6 | Preliminary ALTA survey & title review | Survey | 30 | 2025-03-17 | 2025-04-16 | 2025-04-16 | 0 | 1.2 | 1410 |  | 100% | Complete | Owner / Legal
1.7 | Economic incentives & tax abatement negotiation | Developer | 60 | 2025-02-15 | 2025-04-16 | 2025-04-16 | 0 | 1.1 | 1410 |  | 100% | Complete | Developer
1.8 | Preliminary power interconnection study | Utility eng. | 75 | 2025-02-15 | 2025-05-01 | 2025-05-01 | 0 | 1.1 | 1395 |  | 100% | Complete | Owner / Utility
1.5 | ◆ Site selection decision | — | 0 | 2025-06-05 | 2025-06-05 | 2025-06-05 | 0 | 1.4 | 0 | ● CRITICAL | 100% | Complete | Owner
2 | Acquisition & Entitlements |  | 330 | 2025-06-05 | 2026-05-01 | 2026-05-01 | 0 |  |  |  | 100% | Complete | Owner
2.1 | Purchase & Sale negotiation | Legal | 45 | 2025-06-05 | 2025-07-20 | 2025-07-20 | 0 | 1.5 | 0 | ● CRITICAL | 100% | Complete | Owner / Legal
2.2 | ◆ Land acquisition / closing | — | 0 | 2025-07-20 | 2025-07-20 | 2025-07-20 | 0 | 2.1 | 0 | ● CRITICAL | 100% | Complete | Owner
2.3 | Zoning & land-use approvals | Land-use | 120 | 2025-07-20 | 2025-11-17 | 2025-11-17 | 0 | 2.2 | 0 | ● CRITICAL | 100% | Complete | Owner
2.4 | Environmental permits (wetlands, air, NPDES) | Env. consultant | 110 | 2025-07-20 | 2025-11-07 | 2025-11-07 | 0 | 2.2 | 1205 |  | 100% | Complete | Owner
2.5 | Utility & power capacity agreements | Utility | 150 | 2025-07-20 | 2025-12-17 | 2025-12-17 | 0 | 2.2 | 1165 |  | 100% | Complete | Owner / Utility
2.6 | Site plan & civil permitting | Civil eng. | 75 | 2025-11-17 | 2026-01-31 | 2026-01-31 | 0 | 2.3 | 0 | ● CRITICAL | 100% | Complete | Owner / Civil
2.7 | Building permit application & review | A-E / AHJ | 90 | 2026-01-31 | 2026-05-01 | 2026-05-01 | 0 | 2.6 | 0 | ● CRITICAL | 100% | Complete | Architect
2.9 | Traffic impact study & VDOT approvals | Civil eng. | 90 | 2025-11-17 | 2026-02-15 | 2026-02-15 | 0 | 2.3 | 1105 |  | 100% | Complete | Owner / Civil
2.10 | Stormwater management plan approval | Civil eng. | 75 | 2025-11-17 | 2026-01-31 | 2026-01-31 | 0 | 2.3 | 1120 |  | 100% | Complete | Owner / Civil
2.11 | Design-phase geotechnical borings | Geotech | 45 | 2025-07-20 | 2025-09-03 | 2025-09-03 | 0 | 2.1 | 1270 |  | 100% | Complete | Owner
2.8 | ◆ Building permit issuance | — | 0 | 2026-05-01 | 2026-05-01 | 2026-05-01 | 0 | 2.7 | 0 | ● CRITICAL | 100% | Complete | AHJ
3 | Design & Engineering |  | 315 | 2025-07-20 | 2026-05-31 | 2026-05-31 | 0 |  |  |  | 100% | Complete | Architect / Engineer
3.1 | Programming & design criteria (OPR) | Owner / A-E | 30 | 2025-07-20 | 2025-08-19 | 2025-08-19 | 0 | 2.2 | 0 | ● CRITICAL | 100% | Complete | Owner
3.2 | Schematic Design (SD) | Architect | 60 | 2025-08-19 | 2025-10-18 | 2025-10-18 | 0 | 3.1 | 0 | ● CRITICAL | 100% | Complete | Architect / Eng
3.3 | Design Development (DD) | Architect | 75 | 2025-10-18 | 2026-01-01 | 2026-01-01 | 0 | 3.2 | 0 | ● CRITICAL | 100% | Complete | Architect / Eng
3.4 | Construction Documents (CD) | Architect | 90 | 2026-01-01 | 2026-04-01 | 2026-04-01 | 0 | 3.3 | 0 | ● CRITICAL | 100% | Complete | Architect / Eng
3.5 | MEP & structural coordination / BIM | MEP eng. | 60 | 2026-04-01 | 2026-05-31 | 2026-05-31 | 0 | 3.4 | 0 | ● CRITICAL | 100% | Complete | Engineers
3.7 | Energy modeling & LEED / sustainability design | Sustainability | 60 | 2026-01-01 | 2026-03-02 | 2026-03-02 | 0 | 3.3 | 1090 |  | 100% | Complete | Engineers
3.8 | Commissioning design & Cx specifications | CxA | 45 | 2026-04-01 | 2026-05-16 | 2026-05-16 | 0 | 3.4 | 1015 |  | 100% | Complete | CxA
3.9 | Constructability & value-engineering review | CM | 30 | 2026-04-01 | 2026-05-01 | 2026-05-01 | 0 | 3.4 | 1030 |  | 100% | Complete | CM / GC
3.6 | ◆ Design complete / Issued-for-Construction | — | 0 | 2026-05-31 | 2026-05-31 | 2026-05-31 | 0 | 3.5 | 0 | ● CRITICAL | 100% | Complete | Architect / Eng
4 | Procurement & Long-Lead |  | 300 | 2026-01-01 | 2026-10-28 | 2026-10-28 | 0 |  |  |  | 68.17% | In Progress | CM / GC
4.1 | GC / CM selection & GMP | Owner / CM | 60 | 2026-01-01 | 2026-03-02 | 2026-03-02 | 0 | 3.3 | 0 | ● CRITICAL | 100% | Complete | Owner / CM
4.2 | Trade subcontractor buyout | CM | 90 | 2026-03-02 | 2026-05-31 | 2026-05-31 | 0 | 4.1 | 1000 |  | 100% | Complete | CM / GC
4.3 | ◆ Long-lead equipment release (PO) | — | 0 | 2026-03-02 | 2026-03-02 | 2026-03-02 | 0 | 4.1 | 0 | ● CRITICAL | 100% | Complete | CM
4.4 | MV transformers — fab & deliver | Vendor | 240 | 2026-03-02 | 2026-10-28 | 2026-10-28 | 0 | 4.3 | 0 | ● CRITICAL | 50.42% | In Progress | Vendors / CM
4.5 | MV switchgear — fab & deliver | Vendor | 210 | 2026-03-02 | 2026-09-28 | 2026-09-28 | 0 | 4.3 | 425 |  | 57.62% | In Progress | Vendors / CM
4.6 | LV switchboards/panelboards — fab & deliver | Vendor | 180 | 2026-03-02 | 2026-08-29 | 2026-08-29 | 0 | 4.3 | 545 |  | 67.22% | In Progress | Vendors / CM
4.7 | Generators — fab & deliver | Vendor | 210 | 2026-03-02 | 2026-09-28 | 2026-09-28 | 0 | 4.3 | 335 |  | 57.62% | In Progress | Vendors / CM
4.8 | Gen paralleling switchgear — fab & deliver | Vendor | 200 | 2026-03-02 | 2026-09-18 | 2026-09-18 | 0 | 4.3 | 435 |  | 60.5% | In Progress | Vendors / CM
4.9 | UPS & batteries — fab & deliver | Vendor | 180 | 2026-03-02 | 2026-08-29 | 2026-08-29 | 0 | 4.3 | 545 |  | 67.22% | In Progress | Vendors / CM
4.1 | BESS — fab & deliver | Vendor | 240 | 2026-03-02 | 2026-10-28 | 2026-10-28 | 0 | 4.3 | 0 | ● CRITICAL | 50.42% | In Progress | Vendors / CM
4.11 | Busway & PDUs — fab & deliver | Vendor | 160 | 2026-03-02 | 2026-08-09 | 2026-08-09 | 0 | 4.3 | 565 |  | 75.62% | In Progress | Vendors / CM
4.12 | Chillers (centrifugal + air-cooled) — deliver | Vendor | 200 | 2026-03-02 | 2026-09-18 | 2026-09-18 | 0 | 4.3 | 345 |  | 60.5% | In Progress | Vendors / CM
4.13 | Cooling towers — fab & deliver | Vendor | 170 | 2026-03-02 | 2026-08-19 | 2026-08-19 | 0 | 4.3 | 495 |  | 71.18% | In Progress | Vendors / CM
4.14 | CRAH / in-row units — deliver | Vendor | 150 | 2026-03-02 | 2026-07-30 | 2026-07-30 | 0 | 4.3 | 615 |  | 80.67% | In Progress | Vendors / CM
4.15 | CDUs / direct liquid cooling — deliver | Vendor | 180 | 2026-03-02 | 2026-08-29 | 2026-08-29 | 0 | 4.3 | 585 |  | 67.22% | In Progress | Vendors / CM
4.16 | AHUs & air-side economizers — deliver | Vendor | 160 | 2026-03-02 | 2026-08-09 | 2026-08-09 | 0 | 4.3 | 505 |  | 75.62% | In Progress | Vendors / CM
4.17 | Fuel system (tanks & pumps) — deliver | Vendor | 140 | 2026-03-02 | 2026-07-20 | 2026-07-20 | 0 | 4.3 | 950 |  | 86.43% | In Progress | Vendors / CM
4.18 | IT racks, cabling & network gear — deliver | Vendor | 120 | 2026-03-02 | 2026-06-30 | 2026-06-30 | 0 | 4.3 | 575 |  | 100% | Complete | Owner IT vendor
4.20 | Structural steel — fab & deliver | Vendor | 180 | 2026-03-02 | 2026-08-29 | 2026-08-29 | 0 | 4.3 | 910 |  | 67.22% | In Progress | Vendors / CM
4.21 | Submittal & shop-drawing review | A-E / CM | 90 | 2026-05-31 | 2026-08-29 | 2026-08-29 | 0 | 4.2 | 910 |  | 34.44% | In Progress | Architect / Eng
4.22 | Owner-furnished equipment coordination | Owner / CM | 120 | 2026-03-02 | 2026-06-30 | 2026-06-30 | 0 | 4.3 | 970 |  | 100% | Complete | Owner / CM
4.19 | ◆ All major equipment on site | — | 0 | 2026-10-28 | 2026-10-28 | 2026-10-28 | 0 | 4.10 / 4.4 | 850 |  | 0% | Not Started | CM
5 | Pre-Construction & Mobilization |  | 55 | 2026-05-01 | 2026-06-25 | 2026-06-25 | 0 |  |  |  | 100% | Complete | GC
5.1 | Site mobilization & temp facilities | GC | 30 | 2026-05-01 | 2026-05-31 | 2026-05-31 | 0 | 2.8 | 0 | ● CRITICAL | 100% | Complete | GC
5.2 | Erosion control & SWPPP | Civil crew | 20 | 2026-05-31 | 2026-06-20 | 2026-06-20 | 0 | 5.1 | 0 | ● CRITICAL | 100% | Complete | GC
5.3 | Survey, staking & layout | Survey | 15 | 2026-05-31 | 2026-06-15 | 2026-06-15 | 0 | 5.1 | 985 |  | 100% | Complete | GC
5.4 | Construction power & water | Electricians | 25 | 2026-05-31 | 2026-06-25 | 2026-06-25 | 0 | 5.1 | 975 |  | 100% | Complete | GC
5.5 | Construction fencing & access control / badging | GC | 20 | 2026-05-31 | 2026-06-20 | 2026-06-20 | 0 | 5.1 | 980 |  | 100% | Complete | GC
5.6 | Material laydown & crane / logistics plan | GC | 15 | 2026-05-31 | 2026-06-15 | 2026-06-15 | 0 | 5.1 | 985 |  | 100% | Complete | GC
5.7 | Pre-construction safety & QA/QC program setup | GC | 20 | 2026-05-31 | 2026-06-20 | 2026-06-20 | 0 | 5.1 | 980 |  | 100% | Complete | GC / Safety
6 | Site Work & Civil |  | 700 | 2026-06-20 | 2028-05-20 | 2028-05-20 | 0 |  |  |  | 3.099% | In Progress | Civil / GC
6.1 | Clearing & demolition | Civil crew | 30 | 2026-06-20 | 2026-07-20 | 2026-07-20 | 0 | 5.2 | 0 | ● CRITICAL | 36.67% | In Progress | Civil sub
6.2 | Mass grading & earthwork | Civil crew | 45 | 2026-07-20 | 2026-09-03 | 2026-09-03 | 0 | 6.1 | 0 | ● CRITICAL | 0% | Not Started | Civil sub
6.3 | Mass excavation | Civil crew | 40 | 2026-09-03 | 2026-10-13 | 2026-10-13 | 0 | 6.2 | 0 | ● CRITICAL | 0% | Not Started | Civil sub
6.4 | Underground utilities (storm/san/water) | Civil crew | 55 | 2026-10-13 | 2026-12-07 | 2026-12-07 | 0 | 6.3 | 0 | ● CRITICAL | 0% | Not Started | Civil sub
6.5 | Underground electrical duct banks | Electricians | 45 | 2026-12-07 | 2027-01-21 | 2027-01-21 | 0 | 6.4 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
6.8 | Erosion & sediment control / SWPPP | Civil crew | 20 | 2026-07-20 | 2026-08-09 | 2026-08-09 | 0 | 6.1 | 930 |  | 0% | Not Started | Civil sub
6.9 | Site security fencing & gates | Fencing | 15 | 2026-07-20 | 2026-08-04 | 2026-08-04 | 0 | 6.1 | 935 |  | 0% | Not Started | Site security
6.10 | Stormwater detention basin | Civil crew | 35 | 2026-09-03 | 2026-10-08 | 2026-10-08 | 0 | 6.2 | 870 |  | 0% | Not Started | Civil sub
6.6 | Site paving & access roads | Paving crew | 40 | 2027-01-21 | 2027-03-02 | 2027-03-02 | 0 | 6.5 | 725 |  | 0% | Not Started | Civil sub
6.7 | Landscaping & site finishes | Landscape | 30 | 2028-04-20 | 2028-05-20 | 2028-05-20 | 0 | 11.5 | 280 |  | 0% | Not Started | Civil sub
7 | Foundations & Structure |  | 320 | 2026-10-13 | 2027-08-29 | 2027-08-29 | 0 |  |  |  | 0% | Not Started | GC / Structural
7.1 | Deep foundations / piles | Pile crew | 45 | 2026-10-13 | 2026-11-27 | 2026-11-27 | 0 | 6.3 | 0 | ● CRITICAL | 0% | Not Started | Concrete sub
7.2 | Foundations & grade beams | Concrete | 60 | 2026-11-27 | 2027-01-26 | 2027-01-26 | 0 | 7.1 | 0 | ● CRITICAL | 0% | Not Started | Concrete sub
7.3 | Slab-on-grade | Concrete | 40 | 2027-01-26 | 2027-03-07 | 2027-03-07 | 0 | 7.2 | 0 | ● CRITICAL | 0% | Not Started | Concrete sub
7.4 | Structural steel erection | Iron workers | 90 | 2027-03-07 | 2027-06-05 | 2027-06-05 | 0 | 7.3 | 0 | ● CRITICAL | 0% | Not Started | Steel erector
7.5 | Metal deck & concrete fill | Iron workers | 40 | 2027-06-05 | 2027-07-15 | 2027-07-15 | 0 | 7.4 | 0 | ● CRITICAL | 0% | Not Started | Steel erector
7.6 | Roof structure & framing | Iron workers | 45 | 2027-07-15 | 2027-08-29 | 2027-08-29 | 0 | 7.5 | 0 | ● CRITICAL | 0% | Not Started | Steel erector
7.8 | Anchor bolts, embeds & baseplates | Concrete | 20 | 2027-01-26 | 2027-02-15 | 2027-02-15 | 0 | 7.2 | 740 |  | 0% | Not Started | Concrete sub
7.9 | Under-slab waterproofing & vapor barrier | Waterproofing | 15 | 2027-01-26 | 2027-02-10 | 2027-02-10 | 0 | 7.2 | 745 |  | 0% | Not Started | Waterproofing sub
7.10 | Fireproofing of structural steel | Fireproofing | 30 | 2027-06-05 | 2027-07-05 | 2027-07-05 | 0 | 7.4 | 600 |  | 0% | Not Started | Fireproofing sub
7.7 | ◆ Building dried-in | — | 0 | 2027-08-29 | 2027-08-29 | 2027-08-29 | 0 | 7.6 | 0 | ● CRITICAL | 0% | Not Started | GC
8 | Building Envelope |  | 150 | 2027-06-05 | 2027-11-02 | 2027-11-02 | 0 |  |  |  | 0% | Not Started | Envelope sub
8.1 | Exterior wall framing / cladding | Envelope crew | 75 | 2027-06-05 | 2027-08-19 | 2027-08-19 | 0 | 7.4 | 0 | ● CRITICAL | 0% | Not Started | Envelope sub
8.2 | Insulation & vapor barrier | Envelope crew | 35 | 2027-08-19 | 2027-09-23 | 2027-09-23 | 0 | 8.1 | 520 |  | 0% | Not Started | Envelope sub
8.3 | Roofing & waterproofing | Roofers | 45 | 2027-08-29 | 2027-10-13 | 2027-10-13 | 0 | 7.6 | 0 | ● CRITICAL | 0% | Not Started | Roofing sub
8.4 | Doors, windows & louvers | Glaziers | 40 | 2027-08-19 | 2027-09-28 | 2027-09-28 | 0 | 8.1 | 515 |  | 0% | Not Started | Glazing sub
8.6 | Air & vapor barrier inspection & testing | Envelope crew | 15 | 2027-09-23 | 2027-10-08 | 2027-10-08 | 0 | 8.2 | 505 |  | 0% | Not Started | Envelope sub
8.7 | Firestopping & exterior sealants | Caulkers | 20 | 2027-10-13 | 2027-11-02 | 2027-11-02 | 0 | 8.3 | 480 |  | 0% | Not Started | Envelope sub
8.8 | Louvers & penetration weatherproofing | Envelope crew | 15 | 2027-09-28 | 2027-10-13 | 2027-10-13 | 0 | 8.4 | 500 |  | 0% | Not Started | Envelope sub
8.5 | ◆ Building weather-tight | — | 0 | 2027-10-13 | 2027-10-13 | 2027-10-13 | 0 | 8.3 | 0 | ● CRITICAL | 0% | Not Started | GC
9 | Electrical / Power Infrastructure |  | 405 | 2027-07-15 | 2028-08-23 | 2028-08-23 | 0 |  |  |  | 0% | Not Started | Electrical sub
9.1 | Utility substation & switchgear install | Electricians | 90 | 2027-08-29 | 2027-11-27 | 2027-11-27 | 0 | 7.7 / 4.4 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
9.2 | Main switchgear install | Electricians | 90 | 2027-11-27 | 2028-02-25 | 2028-02-25 | 0 | 9.1 / 4.5 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
9.3 | LV switchboards & panelboards install | Electricians | 75 | 2028-02-25 | 2028-05-10 | 2028-05-10 | 0 | 9.2 / 4.6 | 290 |  | 0% | Not Started | Electrical sub
9.4 | Generator plant install & fuel system | Electricians | 90 | 2027-08-29 | 2027-11-27 | 2027-11-27 | 0 | 7.7 / 4.7 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
9.5 | Generator paralleling switchgear install | Electricians | 60 | 2027-11-27 | 2028-01-26 | 2028-01-26 | 0 | 9.4 / 4.8 | 395 |  | 0% | Not Started | Electrical sub
9.6 | UPS systems & battery install | Electricians | 75 | 2028-02-25 | 2028-05-10 | 2028-05-10 | 0 | 9.2 / 4.9 | 105 |  | 0% | Not Started | Electrical sub
9.7 | BESS install | Electricians | 60 | 2028-02-25 | 2028-04-25 | 2028-04-25 | 0 | 9.2 / 4.10 | 305 |  | 0% | Not Started | Electrical sub
9.8 | MV/LV distribution & busway install | Electricians | 110 | 2028-02-25 | 2028-06-14 | 2028-06-14 | 0 | 9.2 / 4.11 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
9.9 | PDUs & remote power panels install | Electricians | 70 | 2028-06-14 | 2028-08-23 | 2028-08-23 | 0 | 9.8 / 4.11 | 0 | ● CRITICAL | 0% | Not Started | Electrical sub
9.1 | Grounding & lightning protection | Electricians | 40 | 2027-07-15 | 2027-08-24 | 2027-08-24 | 0 | 7.5 | 550 |  | 0% | Not Started | Electrical sub
9.12 | Cable tray, conduit & raceway infrastructure | Electricians | 40 | 2027-11-27 | 2028-01-06 | 2028-01-06 | 0 | 9.1 | 415 |  | 0% | Not Started | Electrical sub
9.13 | MV cable terminations & hi-pot testing | Electricians | 30 | 2028-06-14 | 2028-07-14 | 2028-07-14 | 0 | 9.8 | 225 |  | 0% | Not Started | Electrical sub
9.14 | Arc-flash study & relay coordination | Power engineer | 30 | 2028-02-25 | 2028-03-26 | 2028-03-26 | 0 | 9.2 | 335 |  | 0% | Not Started | Commissioning agent
9.11 | ◆ Power-on / energization | — | 0 | 2028-08-23 | 2028-08-23 | 2028-08-23 | 0 | 9.9 / 9.6 | 0 | ● CRITICAL | 0% | Not Started | Electrical / Utility
10 | Mechanical / Cooling |  | 390 | 2027-08-29 | 2028-09-22 | 2028-09-22 | 0 |  |  |  | 0% | Not Started | Mechanical sub
10.1 | Central plant — chillers install | Pipefitters | 120 | 2027-08-29 | 2027-12-27 | 2027-12-27 | 0 | 7.7 / 4.12 | 0 | ● CRITICAL | 0% | Not Started | Mechanical sub
10.2 | Cooling towers / heat rejection install | Pipefitters | 90 | 2027-12-27 | 2028-03-26 | 2028-03-26 | 0 | 10.1 / 4.13 | 335 |  | 0% | Not Started | Mechanical sub
10.3 | Chilled-water piping distribution | Pipefitters | 100 | 2027-12-27 | 2028-04-05 | 2028-04-05 | 0 | 10.1 | 0 | ● CRITICAL | 0% | Not Started | Mechanical sub
10.4 | CRAH / in-row cooling install | Pipefitters | 80 | 2028-04-05 | 2028-06-24 | 2028-06-24 | 0 | 10.3 / 4.14 | 0 | ● CRITICAL | 0% | Not Started | Mechanical sub
10.5 | CDU / direct liquid cooling install | Pipefitters | 70 | 2028-04-05 | 2028-06-14 | 2028-06-14 | 0 | 10.3 / 4.15 | 255 |  | 0% | Not Started | Mechanical sub
10.6 | AHUs & air-side economizers install | Pipefitters | 80 | 2027-12-27 | 2028-03-16 | 2028-03-16 | 0 | 10.1 / 4.16 | 345 |  | 0% | Not Started | Mechanical sub
10.7 | Pumps & thermal storage install | Pipefitters | 70 | 2027-12-27 | 2028-03-06 | 2028-03-06 | 0 | 10.1 | 355 |  | 0% | Not Started | Mechanical sub
10.1 | Condenser / heat-rejection water piping | Pipefitters | 45 | 2028-03-26 | 2028-05-10 | 2028-05-10 | 0 | 10.2 | 290 |  | 0% | Not Started | Mechanical sub
10.11 | Refrigerant & glycol charging / pressure test | Pipefitters | 30 | 2028-04-05 | 2028-05-05 | 2028-05-05 | 0 | 10.3 | 295 |  | 0% | Not Started | Mechanical sub
10.12 | Leak detection & containment monitoring | Controls tech | 30 | 2028-06-24 | 2028-07-24 | 2028-07-24 | 0 | 10.4 | 215 |  | 0% | Not Started | Controls sub
10.8 | BMS / controls integration | Controls tech | 90 | 2028-06-24 | 2028-09-22 | 2028-09-22 | 0 | 10.4 | 0 | ● CRITICAL | 0% | Not Started | Controls sub
10.9 | ◆ Mechanical water-on | — | 0 | 2028-09-22 | 2028-09-22 | 2028-09-22 | 0 | 10.8 | 15 |  | 0% | Not Started | Mechanical
11 | Interior Fit-Out / White Space |  | 320 | 2027-10-13 | 2028-08-28 | 2028-08-28 | 0 |  |  |  | 0% | Not Started | GC / Trades
11.1 | Interior partitions & framing | Drywall | 60 | 2027-10-13 | 2027-12-12 | 2027-12-12 | 0 | 8.5 | 0 | ● CRITICAL | 0% | Not Started | GC / Drywall
11.2 | Raised access floor | Floor crew | 45 | 2027-12-12 | 2028-01-26 | 2028-01-26 | 0 | 11.1 | 0 | ● CRITICAL | 0% | Not Started | Fit-out sub
11.3 | Hot/cold aisle containment | Fit-out crew | 40 | 2028-01-26 | 2028-03-06 | 2028-03-06 | 0 | 11.2 | 0 | ● CRITICAL | 0% | Not Started | Fit-out sub
11.4 | Fire protection (pre-action/clean agent) | Sprinkler | 60 | 2027-12-12 | 2028-02-10 | 2028-02-10 | 0 | 11.1 | 380 |  | 0% | Not Started | Fire-protection sub
11.5 | Interior finishes (paint, ceilings) | Finishers | 45 | 2028-03-06 | 2028-04-20 | 2028-04-20 | 0 | 11.3 | 0 | ● CRITICAL | 0% | Not Started | GC
11.7 | Overhead cable pathway & ladder rack | Fit-out crew | 30 | 2028-01-26 | 2028-02-25 | 2028-02-25 | 0 | 11.2 | 365 |  | 0% | Not Started | Fit-out sub
11.8 | Under-floor leak detection | Controls tech | 20 | 2028-01-26 | 2028-02-15 | 2028-02-15 | 0 | 11.2 | 375 |  | 0% | Not Started | Controls sub
11.9 | White-space signage, labeling & asset tagging | Fit-out crew | 20 | 2028-04-20 | 2028-05-10 | 2028-05-10 | 0 | 11.5 | 290 |  | 0% | Not Started | Fit-out sub
11.6 | Data-hall power (PDU, busway, whips) | Electricians | 75 | 2028-06-14 | 2028-08-28 | 2028-08-28 | 0 | 11.2 / 9.8 | 180 |  | 0% | Not Started | Electrical sub
12 | IT & Network Integration |  | 215 | 2028-01-26 | 2028-08-28 | 2028-08-28 | 0 |  |  |  | 0% | Not Started | IT / Owner vendor
12.1 | Structured cabling backbone | Cabling crew | 60 | 2028-01-26 | 2028-03-26 | 2028-03-26 | 0 | 11.2 / 4.18 | 0 | ● CRITICAL | 0% | Not Started | Cabling sub
12.2 | Server racks & cabinets install | IT vendor | 45 | 2028-03-26 | 2028-05-10 | 2028-05-10 | 0 | 12.1 / 4.18 | 0 | ● CRITICAL | 0% | Not Started | Owner IT vendor
12.3 | Network equipment & fiber | IT vendor | 50 | 2028-05-10 | 2028-06-29 | 2028-06-29 | 0 | 12.2 / 4.18 | 0 | ● CRITICAL | 0% | Not Started | Owner IT vendor
12.4 | DCIM / EPMS integration | Controls tech | 60 | 2028-06-29 | 2028-08-28 | 2028-08-28 | 0 | 12.3 | 85 |  | 0% | Not Started | Owner IT vendor
12.6 | Fiber backbone splicing & OTDR testing | Cabling crew | 25 | 2028-06-29 | 2028-07-24 | 2028-07-24 | 0 | 12.3 | 215 |  | 0% | Not Started | Cabling sub
12.7 | Server burn-in & validation | IT vendor | 40 | 2028-05-10 | 2028-06-19 | 2028-06-19 | 0 | 12.2 | 250 |  | 0% | Not Started | Owner IT vendor
12.8 | Network config & VLAN/routing | IT vendor | 30 | 2028-06-29 | 2028-07-29 | 2028-07-29 | 0 | 12.3 | 210 |  | 0% | Not Started | Owner IT vendor
12.5 | Security (access control & CCTV) | Security tech | 55 | 2028-04-20 | 2028-06-14 | 2028-06-14 | 0 | 11.5 | 255 |  | 0% | Not Started | Security sub
13 | Commissioning (Cx) |  | 960 | 2026-05-31 | 2029-01-15 | 2029-01-15 | 0 |  |  |  | 12.65% | In Progress | Commissioning Agent
13.1 | Cx plan & submittals review | CxA | 45 | 2026-05-31 | 2026-07-15 | 2026-07-15 | 0 | 3.6 | 955 |  | 68.89% | In Progress | CxA
13.2 | Lvl 1-2 factory & component testing | CxA | 45 | 2028-08-23 | 2028-10-07 | 2028-10-07 | 0 | 9.11 | 0 | ● CRITICAL | 0% | Not Started | CxA
13.3 | Lvl 3 functional performance testing | CxA | 45 | 2028-10-07 | 2028-11-21 | 2028-11-21 | 0 | 13.2 / 10.9 | 0 | ● CRITICAL | 0% | Not Started | CxA
13.4 | Lvl 4 integrated systems test (IST) | CxA | 30 | 2028-11-21 | 2028-12-21 | 2028-12-21 | 0 | 13.3 / 12.4 | 0 | ● CRITICAL | 0% | Not Started | CxA
13.5 | Lvl 5 pull-the-plug / sustained test | CxA | 25 | 2028-12-21 | 2029-01-15 | 2029-01-15 | 0 | 13.4 | 0 | ● CRITICAL | 0% | Not Started | CxA
13.7 | BMS/DCIM points verification & trending | CxA | 20 | 2028-11-21 | 2028-12-11 | 2028-12-11 | 0 | 13.3 | 75 |  | 0% | Not Started | CxA
13.8 | Owner witness & functional sign-off | CxA | 15 | 2028-12-21 | 2029-01-05 | 2029-01-05 | 0 | 13.4 | 50 |  | 0% | Not Started | Owner / CxA
13.9 | Cx documentation & systems manual | CxA | 20 | 2028-12-21 | 2029-01-10 | 2029-01-10 | 0 | 13.4 | 45 |  | 0% | Not Started | CxA
13.6 | ◆ Cx complete / systems accepted | — | 0 | 2029-01-15 | 2029-01-15 | 2029-01-15 | 0 | 13.5 | 0 | ● CRITICAL | 0% | Not Started | Owner / CxA
14 | Closeout & Handover |  | 65 | 2028-12-21 | 2029-02-24 | 2029-02-24 | 0 |  |  |  | 0% | Not Started | GC / Owner
14.1 | Punch list & substantial completion | GC | 30 | 2028-12-21 | 2029-01-20 | 2029-01-20 | 0 | 13.4 | 0 | ● CRITICAL | 0% | Not Started | GC
14.2 | Final inspections & Cert. of Occupancy | AHJ | 20 | 2029-01-20 | 2029-02-09 | 2029-02-09 | 0 | 14.1 | 0 | ● CRITICAL | 0% | Not Started | AHJ / GC
14.3 | As-builts & O&M documentation | GC | 25 | 2029-01-15 | 2029-02-09 | 2029-02-09 | 0 | 13.6 | 15 |  | 0% | Not Started | GC / Owner
14.4 | Owner training | CxA / GC | 20 | 2029-01-15 | 2029-02-04 | 2029-02-04 | 0 | 13.6 | 20 |  | 0% | Not Started | GC / Owner
14.5 | Final cleaning & demobilization | GC | 15 | 2029-02-09 | 2029-02-24 | 2029-02-24 | 0 | 14.2 | 0 | ● CRITICAL | 0% | Not Started | GC
14.7 | Warranty docs & spare-parts turnover | GC | 10 | 2029-02-09 | 2029-02-19 | 2029-02-19 | 0 | 14.3 | 5 |  | 0% | Not Started | GC / Owner
14.8 | Operations & security staff onboarding | Owner | 15 | 2029-02-04 | 2029-02-19 | 2029-02-19 | 0 | 14.4 | 5 |  | 0% | Not Started | Owner
14.9 | Final site & landscape acceptance walk | GC | 10 | 2029-02-09 | 2029-02-19 | 2029-02-19 | 0 | 14.2 | 5 |  | 0% | Not Started | GC / Owner
14.6 | ◆ Site Opening / Go-Live | — | 0 | 2029-02-24 | 2029-02-24 | 2029-02-24 | 0 | 14.5 | 0 | ● CRITICAL | 0% | Not Started | Owner
Formulas:
Task (float) = MIN([Task (float), row below]:E15)

## Schedule Acceleration
SCHEDULE ACCELERATION ANALYSIS — RECOVERING TO Q3 2028
Scenario layered on the realistic master schedule. Day-savings and cost premiums are planning inputs (blue) — the Construction Schedule itself is unchanged. Toggle Include? to model recovery.
Realistic go-live (current master schedule): |  |  | 2029-02-24
Target completion (end of Q3 2028): |  |  | 2028-09-30
Recovery required to hit target: |  |  | 147
Days recovered (selected levers): |  |  | 147
Accelerated go-live (scenario): |  |  | 2028-09-30
Gap after acceleration: |  |  | 0
Total acceleration cost premium: |  |  | 17750000
Cost per day recovered: |  |  | 120748.2993
Target met? |  |  | ✓ YES — meets Q3 2028
# | Acceleration Lever | Mechanism / Activities Affected | Days Saved | Include? | Days Applied | Cost Premium | Cost Applied | Schedule Risk | Rec.
1 | Early long-lead PO release at ~60% DD (owner-funded, at risk) | Release transformers / gensets / BESS before GMP so deliveries stop gating installs | 45 | Y | 45 | 3000000 | 3000000 | Med | ✓
2 | Overlap commissioning (Cx Lvl 1–3) with installation | Component/factory & functional testing concurrent with MEP install | 30 | Y | 30 | 1500000 | 1500000 | Low | ✓
3 | Fast-track electrical & mechanical (2nd shift / parallel crews) | Crash power & cooling install (9.x, 10.x) with added crews + OT | 25 | Y | 25 | 7000000 | 7000000 | Med | ✓
4 | Prefab / modular electrical rooms & cooling skids | Offsite assembly of e-houses, UPS & pump skids | 20 | Y | 20 | 3500000 | 3500000 | Low-Med | ✓
5 | Early sitework under grading / foundation permit | Begin civil & foundations before full building permit issues | 15 | Y | 15 | 750000 | 750000 | Low | ✓
6 | Steel erection acceleration (extra cranes / crew) | Add erection crews & cranes on structural steel (7.4) | 15 | N | 0 | 2500000 | 0 | Med | —
7 | Two-shift interior fit-out & containment | Overtime on white-space build-out (11.x) | 12 | Y | 12 | 2000000 | 2000000 | Low | ✓
TOTAL |  |  |  |  | 147 |  | 17750000
RECOMMENDATION
The 6 selected levers recover 147 days for a ~$17.8M premium (~$121K/day), pulling go-live to Sep 30 2028 — meeting the Q3 2028 target.
Do first (best value, lowest risk): #1 early long-lead release + #2 Cx overlap recover 75 days for $4.5M.
#4 prefab/modular (20d, $3.5M) and #5 early sitework (15d, $0.75M) are low-risk follow-ons.
#3 fast-track MEP is the costliest lever ($7.0M / 25d) — include only if the lower-cost levers fall short.
#6 steel acceleration excluded — limited net critical-path benefit while foundations gate erection.
Caveat: day-savings are critical-path estimates and not perfectly additive; validate on a resource-loaded CPM before committing premiums or at-risk POs.

## Variance Tracker
DATA CENTER — ESTIMATE vs. SUBCONTRACTOR VARIANCE TRACKER
Compare engineer's estimate against subcontractor pricing. Plug Sub Bid in column D; status updates automatically.
# | Division | Budget Estimate | Sub Bid | Variance ($) | Variance (%) | Status | Notes
31 | Earthwork | 25614732 |  | 25614732 | 100% | Awaiting bids
32 | Exterior Improvements | 9371809.4642 |  | 9371809.4642 | 100% | Awaiting bids
33 | Utilities | 63598602.375 |  | 63598602.375 | 100% | Awaiting bids
3 | Concrete | 33466040.3876 |  | 33466040.3876 | 100% | Awaiting bids
5 | Metals / Structural | 40836399.762 |  | 40836399.762 | 100% | Awaiting bids
7 | Thermal & Moisture | 38165650.875 |  | 38165650.875 | 100% | Awaiting bids
21 | Fire Suppression | 22577593.5 |  | 22577593.5 | 100% | Awaiting bids
23 | HVAC / Cooling | 226484248.0019 |  | 226484248.0019 | 100% | Awaiting bids
26 | Electrical / Critical Power | 248147784.9504 |  | 248147784.9504 | 100% | Awaiting bids
8 | Openings | 13742209.9774 |  | 13742209.9774 | 100% | Awaiting bids
9 | Finishes | 33189552 |  | 33189552 | 100% | Awaiting bids
10 | Specialties | 4010233.425 |  | 4010233.425 | 100% | Awaiting bids
27 | IT Infrastructure | 60417387.7013 |  | 60417387.7013 | 100% | Awaiting bids
28 | Security | 15750753.425 |  | 15750753.425 | 100% | Awaiting bids
CX | Commissioning | 47367292.5 |  | 47367292.5 | 100% | Awaiting bids
1 | General Conditions | 42983030.6039 |  | 42983030.6039 | 100% | Awaiting bids
22 | Plumbing | 22312498.5188 |  | 22312498.5188 | 100% | Awaiting bids
SC | Soft Costs / Pre-Con | 113098590 |  | 113098590 | 100% | Awaiting bids
4 | Masonry | 5656068 |  | 5656068 | 100% | Awaiting bids
6 | Wood, Plastics & Composites | 1233678.6 |  | 1233678.6 | 100% | Awaiting bids
11 | Equipment | 1525590 |  | 1525590 | 100% | Awaiting bids
12 | Furnishings | 1217056.5 |  | 1217056.5 | 100% | Awaiting bids
14 | Conveying Equipment | 4104292.5 |  | 4104292.5 | 100% | Awaiting bids
25 | Integrated Automation | 13470732 |  | 13470732 | 100% | Awaiting bids
| TOTAL | 1088341827.0674 | 0 | 1088341827.0674 | 100% | Awaiting bids

## Milestone Tracker
MILESTONE ESTIMATE TRACKER
Tracks the estimate at each design milestone. Use to demonstrate cost evolution to client and explain deltas between gates.
MILESTONE | Class | Accuracy | Date | CSA Estimate | MEP Estimate | Other | Total Estimate | Δ vs Prior | Δ % | $/MW | Drivers / Notes
Concept / Order of Magnitude | Class 5 | −50% / +100% | 2024-12-01 | 248599895.3449 | 549219555.8846 | 183429540.0545 | 981248991.284 | — | — | 10902766.5698 | Order-of-magnitude; $/MW benchmark + program brief
Schematic Design (SD) | Class 4 | −30% / +50% | 2025-06-02 | 259739464.7459 | 573829660.2077 | 191648876.1439 | 1025218001.0975 | 43969009.8135 | 4.481% | 11391311.1233 | Major systems sized; SD set; refined site/MEP loads
Design Development (DD) | Class 3 | −20% / +30% | 2025-11-30 | 269114349.8853 | 594541134.143 | 198566139.1894 | 1062221623.2178 | 37003622.1203 | 3.609% | 11802462.4802 | Equipment selections firmed; envelope + redundancy set
Construction Documents (CD) | Class 2 | −10% / +20% | 2026-05-01 | 275731915.8661 | 609160998.0974 | 203448913.1039 | 1088341827.0674 | 26120203.8496 | 2.459% | 12092686.9674 | Current estimate — full CD set; all systems detailed
GMP / Tender | Class 1 | −5% / +10% | 2026-09-30 | 281246554.1835 | 621344218.0593 | 207517891.366 | 1110108663.6087 | 21766836.5413 | 2% | 12334540.7068 | GC GMP at tender; minor scope adds, escalation locked
Awarded Contract Value | Final | Definitive |  | 0 | 0 | 0 | 0 | — | — | — | Pending GMP acceptance / contract execution
MILESTONE PROGRESSION VS BENCHMARKS
Total Δ Concept→Latest: |  |  |  | 128859672.3248
Total Δ % Concept→Latest: |  |  |  | 13.13%
Live Estimate (CD link): | CD (live → Campus Rollup)
Latest CD Estimate: | 1088341827.0674
• Update each row as design milestones are reached. The Δ vs Prior column flags scope creep, market shifts, and design changes between gates.
• CD row is auto-linked to Campus Rollup totals. Override with hardcode if you need to capture the snapshot at a moment in time.
PROJECT MILESTONE TRACKER — KEY GATES (OWNER / CM / GC)
Schedule gates linked live to the Construction Schedule (single source of truth). Tracks Owner vs CM/GC responsibility, baseline vs forecast dates, float & status. Enter an Actual date as each gate is achieved. | [7 empty] | Data Date: | 2026-07-01
Milestone / Gate | Phase | Responsible | Baseline | Forecast | Actual | Var (d) | Float (d) | Status | Critical? | Owner / CM Action & Notes
Site Selection Decision | 1 · Site Selection | Owner | 2025-06-05 | 2025-06-05 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | Go/no-go; secures power & land basis
Land Acquisition / Closing | 2 · Acquisition | Owner | 2025-07-20 | 2025-07-20 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | Title transfer; unlocks site access
Building Permit Issuance | 2 · Entitlements | Owner / AHJ | 2026-05-01 | 2026-05-01 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | Permit in hand; precondition to NTP
Design Complete / IFC | 3 · Design | Architect / Eng | 2026-05-31 | 2026-05-31 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | IFC set released; basis of construction
Long-Lead Equipment Release (PO) | 4 · Procurement | CM / Owner | 2026-03-02 | 2026-03-02 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | POs placed; protects gear lead times
Construction Start (NTP) | 5 · Pre-Con | Owner → CM | 2026-05-01 | 2026-05-01 |  | 0 | 0 | ◑ Reached — log actual | ● CRITICAL | Owner issues NTP; CM mobilizes
All Major Equipment On Site | 4 · Procurement | CM | 2026-10-28 | 2026-10-28 |  | 0 | 850 | On Track |  | Transformers, gensets, chillers delivered
Building Dried-In | 7 · Structure | CM / GC | 2027-08-29 | 2027-08-29 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Roof/deck done; interiors can start
Building Weather-Tight | 8 · Envelope | CM / GC | 2027-10-13 | 2027-10-13 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Envelope sealed; enables MEP & fit-out
Power-On / Energization | 9 · Electrical | CM / Utility | 2028-08-23 | 2028-08-23 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Permanent power live; supports Cx
Mechanical Water-On | 10 · Mechanical | CM | 2028-09-22 | 2028-09-22 |  | 0 | 15 | On Track |  | Cooling plant operational
Commissioning Complete (Cx Accepted) | 13 · Commissioning | CxA / Owner | 2029-01-15 | 2029-01-15 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Lvl 1-5 done; systems accepted
Substantial Completion | 14 · Closeout | CM / Owner | 2029-01-20 | 2029-01-20 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Punch list; beneficial occupancy
Certificate of Occupancy | 14 · Closeout | AHJ | 2029-02-09 | 2029-02-09 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Legal occupancy granted
Site Opening / Go-Live | 14 · Closeout | Owner | 2029-02-24 | 2029-02-24 |  | 0 | 0 | ▲ On Critical Path | ● CRITICAL | Facility operational; IT load on
MILESTONE SUMMARY — STATUS ROLLUP
Total key gates: |  | 15 |  | Owner-involved gates: |  | 8
On critical path: |  | 13 |  | CM / GC-involved gates: |  | 8
Reached — log actuals: |  | 6 |  | Next gate due: |  | All Major Equipment On Site
Upcoming ≤ 90 days: |  | 0 |  | …forecast date: |  | 2026-10-28
Note on E10: Updated: CD = $328M CSA × 1.021 inflation factor to GMP.
Note on F10: Updated: CD = $1,269M MEP × 1.021 inflation factor to GMP.
Note on G10: Updated: CD = $251M Other × 1.021 inflation factor to GMP.

## Risk & Contingency
RISK REGISTER & MONTE-CARLO CONTINGENCY
Probability and three-point cost impacts (yellow) feed a live EMV roll-up and a Monte-Carlo contingency. P-values are compared to the flat contingency carried in the estimate.
1 · RISK REGISTER (probability × three-point cost impact)
Risk ID | Risk Event | Category | Prob. | Cost Min | Cost Likely | Cost Max | EMV | Response Strategy | Status
R-01 | Long-lead equipment escalation (transformers / MV gear) | Supply Chain | 65% | 8000000 | 18000000 | 35000000 | 13216666.6667 | Early procurement; price lock | Mitigating | 114244722222222
R-02 | Generator / switchgear delivery delay → expedite premium | Supply Chain | 45% | 3000000 | 9000000 | 22000000 | 5100000 | Reserve factory slots | Mitigating | 38865000000000
R-03 | Skilled-labor shortage / wage escalation | Labor | 55% | 6000000 | 15000000 | 30000000 | 9350000 | Early trade buy-out | Open | 85002500000000
R-04 | Utility interconnection delay → temporary power | Utility | 40% | 4000000 | 12000000 | 28000000 | 5866666.6667 | Early utility agreement | Open | 6.1582e+13
R-05 | Permitting / AHJ approval delays | Regulatory | 35% | 2000000 | 6000000 | 15000000 | 2683333.3333 | Pre-application reviews | Mitigating | 1.5958e+13
R-06 | Unforeseen geotechnical / site conditions | Site | 30% | 3000000 | 8000000 | 20000000 | 3100000 | Additional borings | Mitigating | 26240000000000
R-07 | Design development growth (DD → CD) | Design | 60% | 10000000 | 25000000 | 50000000 | 17000000 | Design-to-budget; freeze | Open | 233500000000000
R-08 | Cooling technology change (liquid retrofit) | Scope | 25% | 8000000 | 20000000 | 45000000 | 6083333.3333 | Confirm topology early | Open | 125868055555556
R-09 | Commissioning failures / integrated-test rework | Commissioning | 40% | 3000000 | 9000000 | 18000000 | 4000000 | Robust Cx plan / L5 | Mitigating | 27800000000000
R-10 | Severe weather / force majeure | External | 35% | 2000000 | 7000000 | 20000000 | 3383333.3333 | Schedule float; insurance | Accepted | 2.6295e+13
R-11 | MEP scope gaps / integration coordination | Scope | 50% | 4000000 | 11000000 | 24000000 | 6500000 | MSI; coordination BIM | Mitigating | 5.0833e+13
R-12 | Commodity price volatility (steel / copper) | Market | 55% | 5000000 | 14000000 | 32000000 | 9350000 | Escalation clauses; hedge | Open | 88852500000000
R-13 | Tier / code requirement change | Regulatory | 20% | 6000000 | 16000000 | 40000000 | 4133333.3333 | Owner alignment; alternates | Open | 7.8516e+13
R-14 | Subcontractor default / re-procurement | Commercial | 25% | 5000000 | 13000000 | 30000000 | 4000000 | Prequalification; bonds | Mitigating | 5.4792e+13
| TOTAL EXPECTED (ΣEMV) | [5 empty] | 93766666.6667 |  |  | 1028348333333330
2 · ANALYTICAL ROLL-UP (live — assumes risk independence, normal-sum approx.)
Expected risk cost (ΣEMV) — P50≈ |  | 93766666.6667
Std deviation (√Σσ²) |  | 32067870.7328
P50 — Expected |  | 93766666.6667
P80 contingency |  | 120754986.6754
P90 contingency |  | 134864849.7978
P95 contingency |  | 146515107.235
3 · CONTINGENCY COMPARISON vs the estimate's flat allowance
Base estimate (incl. 10% line contingency) |  | 1088341827.0674
Contingency embedded at 10% line-level |  | 98940166.097
Risk-based contingency (P80) |  | 120754986.6754
P80 as % of de-escalated base |  | 12.2%
Assessment |  | ▲ P80 risk exceeds the flat 10% — consider increasing contingency.
4 · MONTE-CARLO SIMULATION (10,000 iterations — snapshot of current register)
Triangular cost impact × Bernoulli occurrence, summed across risks. Snapshot — re-run after editing the register; validates the live analytical P-values in Section 2.
Simulated Mean |  | 93916776 |  |  |  |  | Contingency ($M) | Frequency
Simulated P10 |  | 52706495 |  |  |  |  | 5.7 | 15
Simulated P50 |  | 93114335 |  |  |  |  | 17 | 47
Simulated P80 |  | 121019782 |  |  |  |  | 28.3 | 176
Simulated P90 |  | 136021396 |  |  |  |  | 39.6 | 373
Simulated P95 |  | 147986771 |  |  |  |  | 50.9 | 627
[7 empty] | 62.2 | 894
[7 empty] | 73.5 | 1209
[7 empty] | 84.8 | 1357
[7 empty] | 96.1 | 1384
[7 empty] | 107.4 | 1220
[7 empty] | 118.8 | 960
[7 empty] | 130.1 | 728
[7 empty] | 141.4 | 474
[7 empty] | 152.7 | 271
[7 empty] | 164 | 132
[7 empty] | 175.3 | 83

## Change Order Log
CHANGE ORDER & CONTINGENCY DRAWDOWN LOG
Tracks change orders against the carried contingency. The running balance falls only for COs that are Approved AND funded from Contingency. Yellow = inputs.
Contingency budget (carried 10%): |  |  | 98940166.097
1 · CHANGE ORDER LOG
CO # | Date | Description | Type | Amount | Status | Funding | Cont. Balance
CO-001 | 2026-06-15 | Liquid-cooling provision — B2 data halls | Owner-directed | 8500000 | Approved | Contingency | 90440166.097
CO-002 | 2026-07-02 | Rock excavation — unforeseen subsurface | Unforeseen | 3200000 | Approved | Contingency | 87240166.097
CO-003 | 2026-07-20 | MV switchgear lineup reconfiguration | Design development | 2100000 | Approved | Contingency | 85140166.097
CO-004 | 2026-08-05 | Ductwork / conduit clash rework (L2) | Errors & omissions | 900000 | Approved | Contingency | 84240166.097
CO-005 | 2026-08-18 | Expanded perimeter security scope | Owner-directed | 4500000 | Pending | Owner add | 84240166.097
CO-006 | 2026-09-01 | Utility feeder re-routing per AHJ | Unforeseen | 1800000 | Approved | Contingency | 82440166.097
CO-007 | 2026-09-15 | Fire protection — pre-action upgrade | Design development | 1300000 | Approved | Contingency | 81140166.097
CO-008 | 2026-10-01 | PV-ready roof structural reinforcement | Owner-directed | 2700000 | Pending | Contingency | 81140166.097
CO-009 | 2026-10-20 | Dewatering — high water table | Unforeseen | 1100000 | Approved | Contingency | 80040166.097
CO-010 | 2026-11-05 | BMS / DCIM points expansion | Design development | 600000 | Approved | Contingency | 79440166.097
2 · CONTINGENCY HEALTH
Total change orders submitted |  |  | 26700000
Approved change orders |  |  | 19500000
Pending change orders |  |  | 7200000
Contingency drawn (approved) |  |  | 19500000
Contingency remaining |  |  | 79440166.097
Contingency drawn (%) |  |  | 19.71%
Pending draw on contingency |  |  | 2700000
Status: |  |  | ● Healthy — over half of contingency remains
DRAWDOWN CHART SOURCE
[8 empty] | Point | Remaining | Monitor (50%) | Critical (20%)
[8 empty] | Start | 98940166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-001 | 90440166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-002 | 87240166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-003 | 85140166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-004 | 84240166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-005 | 84240166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-006 | 82440166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-007 | 81140166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-008 | 81140166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-009 | 80040166.097 | 49470083.0485 | 19788033.2194
[8 empty] | CO-010 | 79440166.097 | 49470083.0485 | 19788033.2194

## Total Development Cost
TOTAL DEVELOPMENT COST — OWNER PROJECT BUDGET
Wraps the construction estimate with the owner-level capital the construction budget explicitly excludes (land, off-site utility, owner PM, financing, owner's contingency — see Basis of Estimate exclusions E.1-E.9). Yellow = input.
1 · HARD COSTS (construction — live from the estimate)
Component |  | Amount |  | Basis / source
Construction — CSA (civil/structural/architectural) |  | 275731915.8661 |  | Campus Rollup
Construction — MEP / critical systems |  | 609160998.0974 |  | Campus Rollup
Construction — Cx / GC / soft (in GMP) |  | 203448913.1039 |  | Campus Rollup
Subtotal — Construction (ties to Campus Rollup) |  | 1088341827.0674 |  | Ties to Campus Rollup total
2 · OWNER SOFT COSTS & OTHER CAPITAL (owner-level adds)
Component |  | Amount | Basis | Notes
Land acquisition & assemblage |  | 80000000 | — | ~110 ac NoVA campus parcel
Off-site power / utility interconnection & substation |  | 117000000 | — | 90 MW interconnect; BOE excl. E.2
Owner's project management / owner's rep |  | 27208545.6767 | 2.5% | staff, controls, owner CM
Owner consultants (CxA, geotech, survey, 3rd-party) |  | 16325127.406 | 1.5% | independent of GMP scope
Entitlements, permits & jurisdictional fees (owner) |  | 9500000 | — | proffers / impact fees
FF&E & owner-furnished equipment |  | 6500000 | — | NOC, spares, tooling
IT fit-out / OFCI (servers, network, racks) |  | 0 | — | tenant / separate IT capex
Legal, title, closing & financing fees |  | 12000000 | — | lender, counsel, closing
Subtotal A — Hard + owner soft costs |  | 1356875500.1501
3 · FINANCING — INTEREST DURING CONSTRUCTION (IDC)
Loan-to-cost (construction loan) |  | 60% |  | share of Subtotal A financed
Construction loan interest rate (annual) |  | 7.5%
Construction duration (months) |  | 30
Average draw factor (avg outstanding) |  | 55%
Interest During Construction (IDC) |  | 83956671.5718 |  | Subtotal A × LTC × rate × (mo/12) × avg draw
Subtotal B — incl. financing |  | 1440832171.7219
4 · OWNER CONTINGENCY & TOTAL
Owner's contingency (on Subtotal B) |  | 72041608.5861 | 5% | carried at owner level (BOE E.9)
TOTAL DEVELOPMENT COST (TDC) |  | 1512873780.308
5 · OWNER CAPITAL METRICS
Total Development Cost — $/MW |  | 16809708.6701
Total Development Cost — $/SF |  | 1891.0922
Total Development Cost — $/W (IT) |  | 16.8097
Construction as % of TDC |  | 71.94%
Owner soft + financing + contingency as % of TDC |  | 28.06%
TDC premium over construction only |  | 424531953.2406
6 · COST STRUCTURE & FINANCEABILITY (CFO · investor · lender view)
Cost bucket |  | Amount | % of TDC
Hard construction cost |  | 1088341827.0674 | 71.94%
Owner soft costs |  | 268533673.0827 | 17.75%
Financing — interest during construction |  | 83956671.5718 | 5.549%
Owner's contingency |  | 72041608.5861 | 4.762%
TOTAL DEVELOPMENT COST |  | 1512873780.308 | 100%
Financeability metric |  | Value | Basis
Permanent senior loan (take-out) |  | 907724268.1848 | 60% LTC — Capital Stack
Sponsor equity required |  | 605149512.1232 | TDC − senior loan
Equity as % of total cost |  | 40%
Hard cost as % of TDC (financeable) |  | 71.94% | lenders often cap soft-cost financing
Owner's contingency as % of hard cost |  | 6.619% | contingency adequacy check
QA — INTERNAL TIE CHECKS
Construction line ties to Campus Rollup total |  | ✅ Tie
TDC = Subtotal B + owner contingency |  | ✅ Tie
— chart source data —
Hard construction | 1088341827.0674
Owner soft costs | 268533673.0827
Financing (IDC) | 83956671.5718
Owner's contingency | 72041608.5861
Note on C28: Construction duration = NTP->substantial completion per Construction Schedule (~30 mo; power-on ~mo28, Cx complete ~mo32). Ties to Draw Schedule & dashboard EVM.

## Sources & Uses
SOURCES & USES OF FUNDS
Reconciles the capital required (Uses = Total Development Cost) against how it is funded (Sources = senior debt + equity). Uses link to the TDC tab; debt links to the Capital Stack tab; equity is the balancing plug.
DEAL AT A GLANCE
Total development cost | 1512873780.308 | Levered IRR (active scenario) | 26.65%
IT capacity — design | 90 | Equity multiple | 5.1974
All-in cost / kW (IT) | 16809.7087 | Loan-to-cost | 60%
Senior debt | 907724268.1848 | Sponsor equity | 605149512.1232
USES OF FUNDS
Component | Amount | % of total | Source
Construction (hard cost) | 1088341827.0674 | 71.94% | Campus Rollup estimate
Land acquisition & assemblage | 80000000 | 5.288% | TDC owner soft costs
Utility interconnection & off-site | 117000000 | 7.734% | TDC owner soft costs
Owner PM, consultants, FF&E, legal | 71533673.0827 | 4.728% | TDC owner soft costs
Financing — interest during construction | 83956671.5718 | 5.549% | TDC financing
Owner's contingency | 72041608.5861 | 4.762% | TDC contingency
TOTAL USES (= Total Development Cost) | 1512873780.308 | 100%
SOURCES OF FUNDS
Component | Amount | % of total | Basis
Senior debt (permanent loan) | 907724268.1848 | 60% | sized in Capital Stack (MIN covenant)
Mezzanine / other debt | 0 | 0% | optional — input
Sponsor equity (balancing) | 605149512.1232 | 40% | plug = Uses − debt
TOTAL SOURCES | 1512873780.308 | 100%
CAPITAL STRUCTURE
Debt (senior + mezz) share | 60%
Equity share | 40%
Loan-to-cost (achieved) | 60%
Stabilized DSCR / debt yield | 2.3726 | 18.17%
QA — INTERNAL TIE CHECKS
Sources = Uses | ✅ Tie
Total Uses = Total Development Cost | ✅ Tie
Equity = Capital Stack equity | ✅ Tie
KEY COST METRICS — NORMALIZED (all-in development cost)
Metric | Value |  | Basis
IT capacity — design (MW) | 90 |  | Design IT load — Power & Space Capacity
Gross building area (SF) | 800000 |  | GBA — Power & Space Capacity
Rack positions (capacity) | 4500 |  | Power & Space Capacity
All-in cost per MW (IT) | 16809708.6701 |  | Total Uses ÷ IT MW
All-in cost per kW (IT) | 16809.7087 |  | Total Uses ÷ IT kW
All-in cost per gross SF | 1891.0922 |  | Total Uses ÷ GBA
All-in cost per rack position | 336194.1734 |  | Total Uses ÷ racks
FINANCING TERMS & COST OF CAPITAL
Metric | Value |  | Basis
Permanent loan rate (all-in) | 6.5% |  | Active scenario — Capital Stack
Loan-to-value (stabilized) | 35.78% |  | Senior loan ÷ stabilized value
Stabilized asset value | 2537308567.0593 |  | Stabilized NOI ÷ exit cap — Capital Stack
Cost of equity (levered) | 12% |  | Active scenario — Capital Stack
Blended cost of capital | 8.7% |  | Debt% × rate + Equity% × Ke
Owner's contingency (% of hard cost) | 6.619% |  | Contingency ÷ construction hard cost
— chart source data —
Construction (hard cost) | 1088341827.0674
Land & assemblage | 80000000
Utility & off-site | 117000000
Owner soft costs | 71533673.0827
Financing (IDC) | 83956671.5718
Contingency | 72041608.5861

## Capital Stack & Returns
CAPITAL STACK & LEVERED RETURNS
Sizes permanent debt to the binding covenant (LTC / LTV / DSCR / debt yield), then computes levered equity returns from the Pro Forma NOI and exit. Shows leverage accretion vs. the unlevered case. Yellow = input.
1 · FINANCING ASSUMPTIONS (yellow = input)
Total Development Cost | 1512873780.308 |  |  | DEAL SNAPSHOT
Stabilized NOI ($/yr) | 164925056.8589 |  |  | Levered IRR |  | 26.65% | Equity multiple |  | 5.1974
Stabilized asset value | 2537308567.0593 |  |  | Unlevered IRR |  | 17.44% | Leverage accretion |  | 920.9656
Max loan-to-cost (LTC) | 60% |  |  | Equity check ($mm) |  | 605.1495 | Senior loan ($mm) |  | 907.7243
Max loan-to-value (LTV, stabilized) | 60% |  |  | Binding covenant |  | LTC cap | Achieved LTC |  | 60%
Min DSCR (stabilized) | 1.4 |  |  | Stabilized DSCR |  | 2.3726 | Debt yield |  | 18.17%
Min debt yield | 9% |  |  | Yield on cost |  | 10.9% | Going-in cap (Yr1) |  | 5.065%
Permanent loan rate (all-in) | 6.5% |  |  | Exit value ($mm) |  | 3165.9738 | Dev. profit ($mm) |  | 1024.4348
Amortization (years) | 30 |  |  | NPV @ Ke ($mm) |  | 788.3081 | Verdict |  | ● Accept — clears equity hurdle
Hold period (years) | 8
Cost of equity (levered discount) | 12%
2 · DEBT SIZING — supportable loan = MIN of constraints
Mortgage constant (annual, K) | 7.658% |  |  | SCENARIO MANAGER (financing environment)
Loan by LTC cap | 907724268.1848 |  |  | Active scenario ▸ |  | Base |  | ▸ active scenario now drives LTC · rate · Ke · DSCR
Loan by LTV cap | 1522385140.2356 |  |  | Driver | Downside | Base | Upside | Custom
Loan by DSCR | 1538359190.2135 |  |  | Max LTC | 50% | 60% | 65% | 60%
Loan by debt yield | 1832500631.765 |  |  | Loan rate | 7.75% | 6.5% | 5.75% | 6.5%
Supportable senior loan (MIN) | 907724268.1848 |  |  | Cost of equity | 13.5% | 12% | 11% | 12%
Binding constraint | LTC cap |  |  | Min DSCR | 1.55 | 1.4 | 1.3 | 1.4
Sponsor equity required | 605149512.1232
Annual debt service | 69511202.7221 |  |  | OUTCOMES (live) | Downside | Base | Upside | Custom
Achieved LTC / LTV | 60% | 35.78% | (LTC / LTV) | Levered IRR | 23.34% | 26.65% | 29.02% | 26.65%
Stabilized DSCR | 2.3726 |  |  | Equity multiple | 4.3566 | 5.1974 | 5.8374 | 5.1974
Debt yield | 18.17% |  |  | Equity ($mm) | 756.4369 | 605.1495 | 529.5058 | 605.1495
|  |  |  | Stab. DSCR | 2.5136 | 2.3726 | 2.3717 | 2.3726
3 · LEVERED CASH FLOW TO EQUITY ($)
Line item | Year 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Net operating income (NOI) |  | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 202837017.1844
Debt service |  | -69511202.7221 | -69511202.7221 | -69511202.7221 | -69511202.7221 | -69511202.7221 | -69511202.7221 | -69511202.7221 | -69511202.7221
Loan balance (end of year) |  | 897215142.8947 | 886022924.4607 | 874103211.8285 | 861408717.8752 | 847889081.815 | 833490669.4108 | 818156360.2004 | 801825320.8913
Net sale proceeds (exit, yr 8) | 8: 3165973781.2992
Loan repayment at exit | 8: -801825320.8913
Levered cash flow to equity | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2497474274.8702
Cumulative equity cash flow | -605149512.1232 | -598027744.075 | -531768956.4843 | -433336346.9447 | -322629487.0606 | -206516085.2983 | -84833945.4016 | 42583994.7738 | 2540058269.644
DSCR (NOI ÷ debt service) |  | 1.1025 | 1.9532 | 2.4161 | 2.5926 | 2.6704 | 2.7505 | 2.8331 | 2.918
Cash-on-cash (pre-tax) |  | 1.177% | 10.95% | 16.27% | 18.29% | 19.19% | 20.11% | 21.06% | 22.03%
4 · LEVERED RETURN METRICS
Levered equity IRR | Year 0: 26.65%
Equity multiple (levered) | Year 0: 5.1974
Average cash-on-cash (yrs 1-8) | Year 0: 16.13%
Levered NPV @ cost of equity | Year 0: 788308105.8406
Equity profit at exit | Year 0: 2540058269.644
Unlevered IRR (for comparison) | Year 0: 17.44%
Leverage accretion (levered − unlevered) | Year 0: 920.9656
Equity verdict | Year 0: ● Accept — clears equity hurdle
5 · SENSITIVITY — LEVERED EQUITY IRR (exit cap × LTC)
Exit cap ↓ / LTC → | Year 0: 50%; 1: 55%; 2: 60%; 3: 65%; 4: 70%
5.5% | Year 0: 26.47%; 1: 27.74%; 2: 29.23%; 3: 30.98%; 4: 33.09%
6% | Year 0: 25.21%; 1: 26.44%; 2: 27.88%; 3: 29.58%; 4: 31.64%
6.5% | Year 0: 24.06%; 1: 25.26%; 2: 26.65%; 3: 28.3%; 4: 30.31%
7% | Year 0: 23.01%; 1: 24.17%; 2: 25.52%; 3: 27.12%; 4: 29.07%
7.5% | Year 0: 22.04%; 1: 23.16%; 2: 24.47%; 3: 26.02%; 4: 27.92%
QA — INTERNAL TIE CHECKS
Senior loan + equity = TDC | Year 0: ✅ Tie
Year-0 outflow = − sponsor equity | Year 0: ✅ Tie
Unlevered link matches Pro Forma | Year 0: ✅ Tie
Center grid = base levered IRR | Year 0: ✅ Tie (LTC binds)
SENSITIVITY ENGINE — do not edit (levered equity CF per exit-cap × LTC combo)
C1/L1 | -756436890.154 | 18706968.5018 | 77843988.0445 | 110017809.9933 | 122292060.3378 | 127698602.2159 | 133267340.3505 | 139003140.629 | 3218328625.4057 | 26.47%
C1/L2 | -680793201.1386 | 12914368.275 | 72051387.8176 | 104225209.7664 | 116499460.1109 | 121906001.9891 | 127474740.1236 | 133210540.4022 | 3145717248.4379 | 27.74%
C1/L3 | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 3073105871.4701 | 29.23%
C1/L4 | -529505823.1078 | 1329167.8213 | 60466187.3639 | 92640009.3127 | 104914259.6572 | 110320801.5354 | 115889539.6699 | 121625339.9485 | 3000494494.5023 | 30.98%
C1/L5 | -453862134.0924 | -4463432.4055 | 54673587.1371 | 86847409.0859 | 99121659.4304 | 104528201.3086 | 110096939.4431 | 115832739.7217 | 2927883117.5345 | 33.09%
C2/L1 | -756436890.154 | 18706968.5018 | 77843988.0445 | 110017809.9933 | 122292060.3378 | 127698602.2159 | 133267340.3505 | 139003140.629 | 2906528177.2474 | 25.21%
C2/L2 | -680793201.1386 | 12914368.275 | 72051387.8176 | 104225209.7664 | 116499460.1109 | 121906001.9891 | 127474740.1236 | 133210540.4022 | 2833916800.2796 | 26.44%
C2/L3 | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2761305423.3118 | 27.88%
C2/L4 | -529505823.1078 | 1329167.8213 | 60466187.3639 | 92640009.3127 | 104914259.6572 | 110320801.5354 | 115889539.6699 | 121625339.9485 | 2688694046.344 | 29.58%
C2/L5 | -453862134.0924 | -4463432.4055 | 54673587.1371 | 86847409.0859 | 99121659.4304 | 104528201.3086 | 110096939.4431 | 115832739.7217 | 2616082669.3762 | 31.64%
C3/L1 | -756436890.154 | 18706968.5018 | 77843988.0445 | 110017809.9933 | 122292060.3378 | 127698602.2159 | 133267340.3505 | 139003140.629 | 2642697028.8058 | 24.06%
C3/L2 | -680793201.1386 | 12914368.275 | 72051387.8176 | 104225209.7664 | 116499460.1109 | 121906001.9891 | 127474740.1236 | 133210540.4022 | 2570085651.838 | 25.26%
C3/L3 | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2497474274.8702 | 26.65%
C3/L4 | -529505823.1078 | 1329167.8213 | 60466187.3639 | 92640009.3127 | 104914259.6572 | 110320801.5354 | 115889539.6699 | 121625339.9485 | 2424862897.9024 | 28.3%
C3/L5 | -453862134.0924 | -4463432.4055 | 54673587.1371 | 86847409.0859 | 99121659.4304 | 104528201.3086 | 110096939.4431 | 115832739.7217 | 2352251520.9346 | 30.31%
C4/L1 | -756436890.154 | 18706968.5018 | 77843988.0445 | 110017809.9933 | 122292060.3378 | 127698602.2159 | 133267340.3505 | 139003140.629 | 2416556044.4273 | 23.01%
C4/L2 | -680793201.1386 | 12914368.275 | 72051387.8176 | 104225209.7664 | 116499460.1109 | 121906001.9891 | 127474740.1236 | 133210540.4022 | 2343944667.4595 | 24.17%
C4/L3 | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2271333290.4917 | 25.52%
C4/L4 | -529505823.1078 | 1329167.8213 | 60466187.3639 | 92640009.3127 | 104914259.6572 | 110320801.5354 | 115889539.6699 | 121625339.9485 | 2198721913.5239 | 27.12%
C4/L5 | -453862134.0924 | -4463432.4055 | 54673587.1371 | 86847409.0859 | 99121659.4304 | 104528201.3086 | 110096939.4431 | 115832739.7217 | 2126110536.5561 | 29.07%
C5/L1 | -756436890.154 | 18706968.5018 | 77843988.0445 | 110017809.9933 | 122292060.3378 | 127698602.2159 | 133267340.3505 | 139003140.629 | 2220567191.2992 | 22.04%
C5/L2 | -680793201.1386 | 12914368.275 | 72051387.8176 | 104225209.7664 | 116499460.1109 | 121906001.9891 | 127474740.1236 | 133210540.4022 | 2147955814.3314 | 23.16%
C5/L3 | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2075344437.3637 | 24.47%
C5/L4 | -529505823.1078 | 1329167.8213 | 60466187.3639 | 92640009.3127 | 104914259.6572 | 110320801.5354 | 115889539.6699 | 121625339.9485 | 2002733060.3959 | 26.02%
C5/L5 | -453862134.0924 | -4463432.4055 | 54673587.1371 | 86847409.0859 | 99121659.4304 | 104528201.3086 | 110096939.4431 | 115832739.7217 | 1930121683.4281 | 27.92%
SCENARIO ENGINE — do not edit (recomputes each scenario's levered equity return)
Downside | -756436890.154 | 11019111.0592 | 70156130.6018 | 102329952.5506 | 114604202.8951 | 120010744.7733 | 125579482.9078 | 131315283.1864 | 2620441884.9008 | 23.34% | 4.3566 | 756436890.154 | 756436890.154 | 8.674% | 65613859.7111 | 2.5136 | 682755053.8717
Base | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2497474274.8702 | 26.65% | 5.1974 | 907724268.1848 | 605149512.1232 | 7.658% | 69511202.7221 | 2.3726 | 801825320.8913
Upside | -529505823.1078 | 7092887.6604 | 66229907.203 | 98403729.1518 | 110677979.4963 | 116084521.3745 | 121653259.509 | 127389059.7876 | 2443385836.3722 | 29.02% | 5.8374 | 983367957.2002 | 529505823.1078 | 7.072% | 69540083.1099 | 2.3717 | 855884879.0016
Custom | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2497474274.8702 | 26.65% | 5.1974 | 907724268.1848 | 605149512.1232 | 7.658% | 69511202.7221 | 2.3726 | 801825320.8913
6 · EQUITY DISTRIBUTION WATERFALL (LP / GP)
LP equity share | Year 0: 90%
GP equity share | Year 0: 10%
Preferred return (hurdle, compounded) | bar: Year 0
GP promote (carried interest above pref) | Year 0: 20%
LP equity invested ($) | Year 0: 544634560.9109
GP equity invested ($) | Year 0: 60514951.2123
Annual distribution waterfall ($) | Year 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Total equity cash flow | -605149512.1232 | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 2497474274.8702
Hurdle balance (capital + pref, EoY) | 605149512.1232 | 646439705.0449 | 631896093.8577 | 584015171.8267 | 520029525.6888 | 445518485.9816 | 359477824.9634 | 260818110.7851 | 0
Preferred accrued |  | 48411960.9699 | 51715176.4036 | 50551687.5086 | 46721213.7461 | 41602362.0551 | 35641478.8785 | 28758225.9971 | 20865448.8628
Tier 1 — return of capital + pref |  | 7121768.0482 | 66258787.5908 | 98432609.5396 | 110706859.8841 | 116113401.7623 | 121682139.8968 | 127417940.1754 | 281683559.6479
Tier 2 — residual profit (above pref) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2215790715.2223
LP cash flow | -544634560.9109 | 6409591.2433 | 59632908.8317 | 88589348.5856 | 99636173.8957 | 104502061.586 | 109513925.9071 | 114676146.1578 | 2026147775.861
GP cash flow | -60514951.2123 | 712176.8048 | 6625878.7591 | 9843260.954 | 11070685.9884 | 11611340.1762 | 12168213.9897 | 12741794.0175 | 471326499.0093
Check: LP + GP − total (= 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RETURN BY EQUITY CLASS
| LP | GP
IRR | 60514951.2123 Year 0: 25.41%; 60514951.2123 1: 34.95%
Equity multiple | 60514951.2123 Year 0: 4.7906; 60514951.2123 1: 8.859
Capital invested ($) | 60514951.2123 Year 0: 544634560.9109; 60514951.2123 1: 60514951.2123
Total distributions ($) | 60514951.2123 Year 0: 2609107932.0683; 60514951.2123 1: 536099849.699
Net profit ($) | 60514951.2123 Year 0: 2064473371.1574; 60514951.2123 1: 475584898.4866
GP carried interest (promote on profit above pref) | 60514951.2123 Year 0: 443158143.0445
Deal-level equity IRR (ties to §4 levered IRR) | 60514951.2123 Year 0: 26.65%
Note on B10: Kevin: Scenario-driven: pulls Max LTC from the active scenario (G21). Edit drivers in the Scenario Manager (F23:I26), not here.
Note on B12: Kevin: Scenario-driven: pulls Min DSCR from the active scenario (G21).
Note on B14: Kevin: Scenario-driven: pulls all-in loan rate from the active scenario (G21).
Note on B17: Kevin: Scenario-driven: pulls cost of equity from the active scenario (G21).

## Investment Pro Forma
INVESTMENT PRO FORMA — CAPITAL BUDGETING
Turns the cost estimate into an owner investment case: triple-net (NNN) wholesale lease revenue vs. total development cost, with unlevered IRR / NPV / yield-on-cost and a lease-rate x exit-cap sensitivity. Capex basis links to Total Development Cost; OpEx links to TCO 8-Year (reimbursed per NNN recovery). Yellow = input.
— chart data —
1 · INVESTMENT ASSUMPTIONS (yellow = input) | [10 empty] | Yr 1 | 76632970.7703
Total Development Cost (capex basis) | 1512873780.308 | [9 empty] | Yr 2 | 135769990.3129
IT capacity — leasable (MW) | 90 | [9 empty] | Yr 3 | 167943812.2617
Lease rate ($/kW IT / month) | 165 | [9 empty] | Yr 4 | 180218062.6062
Annual rent escalation | 3% | [9 empty] | Yr 5 | 185624604.4844
Exit / terminal cap rate | 6.5% | [9 empty] | Yr 6 | 191193342.6189
Disposition cost (% of sale) | 1.5% | [9 empty] | Yr 7 | 196929142.8975
Unlevered discount rate (hurdle) | 8.5% | [9 empty] | Yr 8 | 202837017.1844
Stabilized occupancy (for yield-on-cost) | 95%
OpEx recovery (% passed to tenant, NNN) | 95%
2 · LEASE-UP / OCCUPANCY RAMP (yellow = input)
Operating year → |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Occupancy (% of IT capacity leased) |  | 55% | 80% | 92% | 95% | 95% | 95% | 95% | 95%
3 · OPERATING CASH FLOW & RETURNS ($)
Line item | Year 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 8-Yr Total
Leased IT capacity (kW) |  | 49500 | 72000 | 82800 | 85500 | 85500 | 85500 | 85500 | 85500
Effective lease rate ($/kW/mo) |  | 165 | 169.95 | 175.0485 | 180.3 | 185.709 | 191.2802 | 197.0186 | 202.9292
Base rent (net, NNN) |  | 98010000 | 146836800 | 173928189.6 | 184987753.83 | 190537386.4449 | 196253508.0382 | 202141113.2794 | 208205346.6778 | 1400900097.8703
Owner OpEx (maint + staff + tax/ins) |  | -44768647.6015 | -46111707.0295 | -47495058.2404 | -48919909.9876 | -50387507.2873 | -51899132.5059 | -53456106.4811 | -55059789.6755 | -398097858.8088
OpEx recovery (tenant reimbursement) |  | 23391618.3718 | 35044897.3424 | 41510680.9021 | 44150218.7638 | 45474725.3268 | 46838967.0866 | 48244136.0992 | 49691460.1821 | 334346704.0748
Net Operating Income (NOI) |  | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 202837017.1844 | 1337148943.1363
Terminal / residual value (net of disposition) | 3: Forward NOI ÷ exit cap × (1 − disposition cost); 8: 3165973781.2992
Unlevered net cash flow | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836
Cumulative cash flow | -1512873780.308 | -1436240809.5377 | -1300470819.2248 | -1132527006.9631 | -952308944.3569 | -766684339.8725 | -575490997.2535 | -378561854.3561 | 2990248944.1276
NNN structure: tenant pays base rent + reimburses operating expenses; power & water are tenant-metered. Owner NOI = base rent less the owner-retained share of OpEx.
4 · RETURN METRICS
Unlevered IRR | Year 0: 17.44%
NPV @ hurdle | Year 0: 1040538646.478
Equity multiple (MOIC) | Year 0: 2.9765
Simple payback (yrs) | Year 0: 9.1731
Going-in yield (Yr-1 NOI ÷ TDC) | Year 0: 5.065%
Stabilized yield-on-cost | Year 0: 10.9%
Stabilized NOI ($/yr, today $) | Year 0: 164925056.8589
Stabilized asset value (NOI ÷ exit cap) | Year 0: 2537308567.0593
Development profit (value − cost) | Year 0: 1024434786.7513
Development margin (% of cost) | Year 0: 67.71%
Investment verdict | Year 0: ● Accept — clears hurdle
5 · FINANCING & COVERAGE (lender view — links to Capital Stack & Returns)
Senior loan (sized) | Year 0: 907724268.1848; 1: MIN of LTC / LTV / DSCR / debt-yield covenants
Loan-to-cost (LTC) | Year 0: 60%
Loan-to-value (stabilized) | Year 0: 35.78%
All-in loan rate | Year 0: 6.5%
Annual debt service | Year 0: 69511202.7221
Sponsor equity (plug) | Year 0: 605149512.1232
Year-1 DSCR (lease-up) | Year 0: 1.1025; 1: Yr-1 NOI ÷ debt service — ramp coverage
Stabilized DSCR | Year 0: 2.3726
Min DSCR covenant | Year 0: 1.4
Debt yield (stabilized) | Year 0: 18.17%; 1: Stabilized NOI ÷ loan — lender downside metric
Levered IRR (equity) | Year 0: 26.65%
Levered equity multiple | Year 0: 5.1974
6 · SENSITIVITY — UNLEVERED IRR (lease rate × exit cap rate)
Lease $/kW/mo ↓ / Exit cap → | Year 0: 5.5%; 1: 6%; 2: 6.5%; 3: 7%; 4: 7.5%
140.25 | Year 0: 16.21%; 1: 15.26%; 2: 14.41%; 3: 13.64%; 4: 12.93%
152.625 | Year 0: 17.78%; 1: 16.83%; 2: 15.97%; 3: 15.2%; 4: 14.49%
165 | Year 0: 19.26%; 1: 18.3%; 2: 17.44%; 3: 16.67%; 4: 15.96%
177.375 | Year 0: 20.65%; 1: 19.7%; 2: 18.84%; 3: 18.06%; 4: 17.35%
189.75 | Year 0: 21.99%; 1: 21.02%; 2: 20.16%; 3: 19.38%; 4: 18.67%
QA — INTERNAL TIE CHECKS
Capex basis ties to Total Development Cost | Year 0: ✅ Tie
Year-0 outflow = − capex basis | Year 0: ✅ Tie
Center sensitivity cell = headline IRR | Year 0: ✅ Tie
SENSITIVITY ENGINE — do not edit (feeds Section 5)
NOI by operating year, per lease-rate variant
Lease variant | $/kW/mo | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Lease 1 | 140.25 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 171606215.1827
Lease 2 | 152.625 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 187221616.1836
Lease 3 | 165 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 202837017.1844
Lease 4 | 177.375 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 218452418.1852
Lease 5 | 189.75 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 234067819.1861
CF (yr0..8) + IRR per lease×cap combo
L1/C1 | -1512873780.308 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 3337116862.7038 | 16.21%
L1/C2 | -1512873780.308 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 3073324308.7437 | 15.26%
L1/C3 | -1512873780.308 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 2850115224.6237 | 14.41%
L1/C4 | -1512873780.308 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 2658793152.5207 | 13.64%
L1/C5 | -1512873780.308 | 61931470.7703 | 113744470.3129 | 141854583.8217 | 152469899.5317 | 157043996.5177 | 161755316.4132 | 166607975.9056 | 2492980690.0315 | 12.93%
L2/C1 | -1512873780.308 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 3640779628.8937 | 17.78%
L2/C2 | -1512873780.308 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 3352983127.8345 | 16.83%
L2/C3 | -1512873780.308 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 3109463011.5536 | 15.97%
L2/C4 | -1512873780.308 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 2900731483.3129 | 15.2%
L2/C5 | -1512873780.308 | 69282220.7703 | 124757230.3129 | 154899198.0417 | 166343981.069 | 171334300.501 | 176474329.5161 | 181768559.4015 | 2719830825.5043 | 14.49%
L3/C1 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3944442395.0835 | 19.26%
L3/C2 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3632641946.9252 | 18.3%
L3/C3 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.44%
L3/C4 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3142669814.1051 | 16.67%
L3/C5 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 2946680960.9771 | 15.96%
L4/C1 | -1512873780.308 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 4248105161.2733 | 20.65%
L4/C2 | -1512873780.308 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 3912300766.016 | 19.7%
L4/C3 | -1512873780.308 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 3628158585.4136 | 18.84%
L4/C4 | -1512873780.308 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 3384608144.8973 | 18.06%
L4/C5 | -1512873780.308 | 83983720.7703 | 146782750.3129 | 180988426.4817 | 194092144.1435 | 199914908.4678 | 205912355.7218 | 212089726.3934 | 3173531096.4498 | 17.35%
L5/C1 | -1512873780.308 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 4551767927.4632 | 21.99%
L5/C2 | -1512873780.308 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 4191959585.1067 | 21.02%
L5/C3 | -1512873780.308 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 3887506372.3436 | 20.16%
L5/C4 | -1512873780.308 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 3626546475.6895 | 19.38%
L5/C5 | -1512873780.308 | 91334470.7703 | 157795510.3129 | 194033040.7017 | 207966225.6807 | 214205212.4511 | 220631368.8247 | 227250309.8894 | 3400381231.9226 | 18.67%

## Variance-to-Return
VARIANCE-TO-RETURN ANALYSIS
Translates construction cost variance into owner return language. Baseline returns link from the Investment Pro Forma; live cost signals link from EVM (forecast at completion) and the Variance Tracker (bids). Shows what each $ of cost change does to IRR, yield-on-cost, and NPV. Yellow = input.
1 · BASELINE RETURNS (from Investment Pro Forma)
Baseline Total Development Cost | 1512873780.308
Baseline stabilized NOI ($/yr) | 164925056.8589
Baseline yield-on-cost | 10.9%
Baseline unlevered IRR | 17.44%
Baseline NPV @ hurdle | 1040538646.478
2 · LIVE COST SIGNALS
Forecast variance at completion — VAC (from EVM) | 0 | negative = projected overrun
→ Implied capex overrun (− VAC) | 0
Awarded-bid variance to date (only divisions bid) | 0 | positive = under budget (savings)
→ Implied capex change from bids (− variance) | 0
Manual cost-change scenario (Δ capex $) | 10000000
3 · COST VARIANCE → RETURN BRIDGE
Scenario | Δ Capex ($) | New TDC | Yield-on-Cost | Δ YoC | Unlevered IRR | Δ IRR | NPV @ hurdle | Δ NPV
Cost −5% | -75643689.0154 | 1437230091.2926 | 11.48% | 57.376 | 18.39% | 94.6588 | 1116182335.4934 | 75643689.0154
Cost −2.5% | -37821844.5077 | 1475051935.8003 | 11.18% | 27.9524 | 17.91% | 46.5468 | 1078360490.9857 | 37821844.5077
Baseline (0) | 0 | 1512873780.308 | 10.9% | 0 | 17.44% | 0 | 1040538646.478 | 0
Cost +2.5% | 37821844.5077 | 1550695624.8157 | 10.64% | -26.5889 | 16.99% | -45.073 | 1002716801.9704 | -37821844.5077
Cost +5% | 75643689.0154 | 1588517469.3234 | 10.38% | -51.9116 | 16.55% | -88.7559 | 964894957.4626 | -75643689.0154
Cost +10% | 151287378.0308 | 1664161158.3388 | 9.91% | -99.104 | 15.72% | -172.2534 | 889251268.4472 | -151287378.0308
Live: EVM forecast overrun | 0 | 1512873780.308 | 10.9% | 0 | 17.44% | 0 | 1040538646.478 | 0
Live: bid variance to date | 0 | 1512873780.308 | 10.9% | 0 | 17.44% | 0 | 1040538646.478 | 0
Manual scenario | 10000000 | 1522873780.308 | 10.83% | -7.1585 | 17.32% | -12.057 | 1030538646.478 | -10000000
4 · RULE OF THUMB (per +$10M of capex)
Δ unlevered IRR per +$10M capex | -12.057
Δ yield-on-cost per +$10M capex | -7.1585
Δ NPV per +$10M capex | -10000000
Readout
Every $10M of capex change moves unlevered IRR by ~12 bps and yield-on-cost by ~7 bps; NPV moves $10M one-for-one. Current EVM forecast implies a $0M capex swing vs budget.
QA — INTERNAL TIE CHECKS
Baseline row IRR = Pro Forma IRR | ✅ Tie
Δ NPV at baseline = 0 | ✅ Tie
New TDC at baseline = baseline TDC | ✅ Tie
ENGINE — do not edit (CF yr0..8 per scenario; operating CF held = Pro Forma, capex flexed)
scn1 | -1437230091.2926 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 18.39%
scn2 | -1475051935.8003 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.91%
scn3 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.44%
scn4 | -1550695624.8157 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 16.99%
scn5 | -1588517469.3234 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 16.55%
scn6 | -1664161158.3388 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 15.72%
scn7 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.44%
scn8 | -1512873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.44%
scn9 | -1522873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.32%
+$10M unit | -1522873780.308 | 76632970.7703 | 135769990.3129 | 167943812.2617 | 180218062.6062 | 185624604.4844 | 191193342.6189 | 196929142.8975 | 3368810798.4836 | 17.32%
— chart source data —
Cost −5% | 94.6588
Cost −2.5% | 46.5468
Baseline | 0
Cost +2.5% | -45.073
Cost +5% | -88.7559
Cost +10% | -172.2534

## IC Summary
INVESTMENT COMMITTEE SUMMARY |  |  |  |  | CONFIDENTIAL — FOR DISCUSSION ONLY
Data Center Template, Northern Virginia · Northern Virginia · owner develop-to-core |  |  |  | Prepared: 17 Jun 2026
90 MW IT · 800,000 SF · Tier III · Class 3 (DD) estimate |  |  |  | RECOMMENDATION
ACCEPT
THE OPPORTUNITY |  | CAPITALIZATION |  | Levered IRR 26.7% · 5.20x equity multiple · Unlevered IRR 17.4%
Location | Northern Virginia | Total Development Cost | 1512873780.308
Capacity (IT MW) | 90 | — per MW | 16809708.6701
Gross building area (SF) | 800000 | Senior debt (perm) | 907724268.1848
Hold period (years) | 8 | Sponsor equity | 605149512.1232
RETURNS — UNLEVERED (PROJECT) |  | RETURNS — LEVERED (EQUITY)
Unlevered IRR | 17.44% | Levered equity IRR | 26.65%
Yield-on-cost (stabilized) | 10.9% | Avg cash-on-cash | 16.13%
Equity multiple | 2.9765 | Equity multiple | 5.1974
Development margin | 67.71% | Leverage accretion | 920.9656
Stabilized DSCR | 2.3726 | Debt yield | 18.17%
VALUE CREATION
Stabilized NOI ($/yr) | 164925056.8589 | Stabilized asset value | 2537308567.0593
Exit cap rate | 6.5% | Development profit | 1024434786.7513
KEY RISKS & POSITION
◆ Cost certainty — EVM forecasts an underrun of $0M at completion (CPI —); owner contingency carried separately in TDC.
◆ Schedule — SPI —; ○ Not started. Long-lead gear (gensets, switchgear, chillers) tracked in Procurement.
◆ Lease-up / market — underwritten at $165/kW/mo NNN, stabilizing at 95% occupancy; revenue gated on hyperscale pre-leasing & power availability.
◆ Leverage / refinance — 2.37x stabilized DSCR and 18.2% debt yield; loan sized to the binding covenant (LTC cap).
RECOMMENDATION
Unlevered (project): ● Accept — clears hurdle Levered (equity): ● Accept — clears equity hurdle
Recommendation: the project clears its 8.5% unlevered hurdle at a 17.4% IRR and a 67.7% development margin; leverage lifts equity IRR to 26.7%. Returns are most sensitive to lease rate, exit cap, and capex — see Variance-to-Return and the sensitivity grids.
Owner investment summary · all figures link live to the model · estimate basis Class 3 (DD) · Confidential — for discussion only
QA — INTERNAL TIE CHECKS
TDC matches Capital Stack & Sources/Uses |  |  | ✅ Tie
Levered IRR ≥ unlevered IRR (accretive) |  |  | ✅ Accretive
— chart source data (off-page) —
Senior debt (perm) | 907724268.1848
Sponsor equity | 605149512.1232
Unlevered IRR (project) | 17.44%
Levered IRR (equity) | 26.65%

## TCO 8-Year
Lifecycle cost: install year + 8 operating years. CapEx pulls from Construction Budget; OpEx is parametric (PUE-driven utility, maintenance, staffing, depreciation). Methodology mirrors HP Labs / TechTarget references.
INPUT ASSUMPTIONS
Total CapEx (from Construction Budget): | 1088341827.0674
IT Load (MW): | 90
Design PUE: | 1.4
Avg Utilization (% of IT load): | 70%
Electricity rate ($/kWh): | 0.075
Hours / year: | 8760
Water cost ($/yr at full load): | 850000
Maintenance % of CapEx (annual): | 2.5%
Staffing cost ($/yr, full ops): | 4500000
Property tax / insurance (% CapEx): | 1.2%
Inflation (annual escalator): | 3%
Useful life for depreciation (yr): | 30
Discount rate (NPV): | 8%
ANNUAL CASH FLOWS
Line Item | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 8-Yr Total
Construction CapEx | 1088341827.0674 | [8 empty] | 1088341827.0674
Electricity (PUE × IT × utilization × hrs × rate) |  | 57947400 | 59685822 | 61476396.66 | 63320688.5598 | 65220309.2166 | 67176918.4931 | 69192226.0479 | 71267992.8293 | 515287753.8067
Water |  | 595000 | 612850 | 631235.5 | 650172.565 | 669677.742 | 689768.0742 | 710461.1164 | 731774.9499 | 5290939.9475
Maintenance & repair |  | 27208545.6767 | 28024802.047 | 28865546.1084 | 29731512.4916 | 30623457.8664 | 31542161.6024 | 32488426.4505 | 33463079.244 | 241947531.4869
Staffing & operations |  | 4500000 | 4635000 | 4774050 | 4917271.5 | 5064789.645 | 5216733.3344 | 5373235.3344 | 5534432.3944 | 40015512.2081
Property tax / insurance |  | 13060101.9248 | 13451904.9826 | 13855462.132 | 14271125.996 | 14699259.7759 | 15140237.5691 | 15594444.6962 | 16062278.0371 | 116134815.1137
Depreciation (straight-line, non-cash) |  | 36278060.9022 | 36278060.9022 | 36278060.9022 | 36278060.9022 | 36278060.9022 | 36278060.9022 | 36278060.9022 | 36278060.9022 | 290224487.218
OpEx Subtotal (cash) |  | 103311047.6015 | 106410379.0295 | 109602690.4004 | 112890771.1124 | 116277494.2458 | 119765819.0732 | 123358793.6454 | 127059557.4547 | 918676552.563
Cumulative Total (CapEx + OpEx) | 1088341827.0674 | 1191652874.6689 | 1298063253.6984 | 1407665944.0989 | 1520556715.2113 | 1636834209.4571 | 1756600028.5303 | 1879958822.1757 | 2007018379.6304 | 2007018379.6304
TCO HEADLINE METRICS
Total CapEx: | 1088341827.0674
Total 8-Year OpEx: | 918676552.563
8-Year TCO (CapEx + OpEx): | 2007018379.6304
OpEx as % of CapEx (8-yr): | 84.41%
Avg Annual OpEx: | 114834569.0704
Year 1 OpEx / MW: | 1147900.5289
Year 1 OpEx as $/kW (annual): | 1147.9005
Lifecycle $/MW (TCO ÷ MW): | 22300204.2181
NPV of OpEx stream @ discount rate: | 652106649.3793
NPV of full TCO (CapEx today + discounted OpEx): | 1740448476.4467
SENSITIVITY — 8-YR TCO ($M) ¦ PUE × Electricity Rate
PUE ↓ / $/kWh → | 0.055 | 0.065 | 0.075 | 0.085 | 0.095
1.2 | 1815.6258 | 1874.5158 | 1933.4058 | 1992.2959 | 2051.1859
1.3 | 1842.617 | 1906.4146 | 1970.2121 | 2034.0096 | 2097.8072
1.4 | 1869.6083 | 1938.3133 | 2007.0184 | 2075.7234 | 2144.4284
1.5 | 1896.5996 | 1970.2121 | 2043.8246 | 2117.4372 | 2191.0497
1.6 | 1923.5908 | 2002.1109 | 2080.6309 | 2159.151 | 2237.671
QC: Center cell of sensitivity = 8-yr TCO above | ✅ Tie
Note on A29: Kevin: Non-cash expense — NOT included in OpEx Subtotal or 8-Year TCO totals below. Shown for accounting (P&L) view only. Cash-basis TCO of $3,017M assumes CapEx is recognized in year 0; depreciation would be the equivalent P&L recognition over 30 years.

## Phased Capital Plan
PHASED MULTI-YEAR CAPITAL PLAN
Sequential 6-building campus deployment. Per-building cost is live from Campus Rollup; Phase 1 (Shared + B1–B3) reconciles to the current estimate. Later phases carry escalation.
1 · UNIT BASIS (live from the estimate)
Cost per building (CSA+MEP+Other) |  |  | 278078401.5414
Shared infrastructure (one-time, full campus) |  |  | 254106622.4431
IT capacity per building |  |  | 30
Annual escalation |  |  | 3.5%
Escalation base year |  |  | 2027
2 · DEPLOYMENT SCHEDULE
Year | Phase / scope | MW added | Base capex (2027$) | Escal. factor | Escalated capex | Cumulative capex | Cum. MW | $/MW (cum)
2026 | Phase 1a — Shared infra + B1 | 30 | 532185023.9845 | 1 | 532185023.9845 | 532185023.9845 | 30 | 17739500.7995
2027 | Phase 1b — Buildings B2 & B3 | 60 | 556156803.0829 | 1 | 556156803.0829 | 1088341827.0674 | 90 | 12092686.9674
2028 | Phase 2 — Building B4 | 30 | 278078401.5414 | 1.035 | 287811145.5954 | 1376152972.6628 | 120 | 11467941.4389
2029 | Phase 3 — Building B5 | 30 | 278078401.5414 | 1.0712 | 297884535.6912 | 1674037508.354 | 150 | 11160250.0557
2030 | Phase 4 — Building B6 | 30 | 278078401.5414 | 1.1087 | 308310494.4404 | 1982348002.7944 | 180 | 11013044.46
| PROGRAM TOTAL (6 buildings + shared) | 180 |  |  | 1982348002.7944
3 · PROGRAM SUMMARY
Total program capex (escalated) |  |  | 1982348002.7944
Total IT capacity at build-out |  |  | 180
Blended $/MW (full campus) |  |  | 11013044.46
Phase 1 capex (reconciles to estimate) |  |  | 1088341827.0674
Phases 2–4 expansion capex |  |  | 894006175.727

## Draw Schedule
DRAW SCHEDULE & CONSTRUCTION PHASING
Monthly cash outlay by CSI division across the 30-month construction window. Figures shown in USD millions ($M). Driven from Construction Budget division subtotals — update inputs there and this schedule rebuilds automatically. Construction trades are distributed on a cubic S-curve within each trade's start/end window; General Conditions are level-loaded and Soft Costs front-loaded. Each division sums to its full budget, so the schedule total ties to the estimate.
Peak Monthly Draw: $55.5M |  |  | Peak Month: Nov-27 |  |  | Avg Monthly Draw: $36.3M
Project Start: May-26 | 2026-05-01 | Construction Duration (mo): |  | 30 |  | Total Construction: |  |  |  | 1088341827.0674
Division | CB Ref | Total ($M) | Start Mo | End Mo | Duration | 2026-05-31 | 2026-06-30 | 2026-07-31 | 2026-08-31 | 2026-09-30 | 2026-10-31 | 2026-11-30 | 2026-12-31 | 2027-01-31 | 2027-02-28 | 2027-03-31 | 2027-04-30 | 2027-05-31 | 2027-06-30 | 2027-07-31 | 2027-08-31 | 2027-09-30 | 2027-10-31 | 2027-11-30 | 2027-12-31 | 2028-01-31 | 2028-02-29 | 2028-03-31 | 2028-04-30 | 2028-05-31 | 2028-06-30 | 2028-07-31 | 2028-08-31 | 2028-09-30 | 2028-10-31
Earthwork (Div 31) |  | 25614732 | 1 | 8 | 8 | 1100633.0156 | 2901668.8594 | 4102359.4219 | 4702704.7031 | 4702704.7031 | 4102359.4219 | 2901668.8594 | 1100633.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Improvements (Div 32) |  | 9371809.4642 | 23 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402694.9379 | 1061650.2909 | 1500953.8595 | 1720605.6438 | 1720605.6438 | 1500953.8595 | 1061650.2909 | 402694.9379
Utilities (Div 33) |  | 63598602.375 | 3 | 15 | 13 | 0 | 0 | 1071073.4128 | 2981636.7977 | 4544825.0218 | 5760638.0849 | 6629075.9872 | 7150138.7286 | 7323826.309 | 7150138.7286 | 6629075.9872 | 5760638.0849 | 4544825.0218 | 2981636.7977 | 1071073.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Concrete (Div 03) |  | 33466040.3876 | 4 | 13 | 10 | 0 | 0 | 0 | 937049.1309 | 2543419.0695 | 3748196.5234 | 4551381.4927 | 4952973.9774 | 4952973.9774 | 4551381.4927 | 3748196.5234 | 2543419.0695 | 937049.1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metals / Structural (Div 05) |  | 40836399.762 | 8 | 16 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1400425.2319 | 3753139.6215 | 5433649.8997 | 6441956.0667 | 6778058.1224 | 6441956.0667 | 5433649.8997 | 3753139.6215 | 1400425.2319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal & Moisture (Div 07) |  | 38165650.875 | 11 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068638.2245 | 2900589.4665 | 4274552.898 | 5190528.519 | 5648516.3295 | 5648516.3295 | 5190528.519 | 4274552.898 | 2900589.4665 | 1068638.2245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing (Div 22) |  | 22312498.5188 | 9 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284277.7589 | 799944.3913 | 1236277.6957 | 1593277.672 | 1870944.3202 | 2069277.6404 | 2188277.6325 | 2227944.2965 | 2188277.6325 | 2069277.6404 | 1870944.3202 | 1593277.672 | 1236277.6957 | 799944.3913 | 284277.7589 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Suppression (Div 21) |  | 22577593.5 | 13 | 25 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380232.5715 | 1058485.2665 | 1613419.2897 | 2045034.6411 | 2353331.3207 | 2538309.3284 | 2599968.6643 | 2538309.3284 | 2353331.3207 | 2045034.6411 | 1613419.2897 | 1058485.2665 | 380232.5715 | 0 | 0 | 0 | 0 | 0
HVAC / Cooling (Div 23) |  | 226484248.0019 | 10 | 28 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1816100.5453 | 5184141.5565 | 8155942.4488 | 10731503.2221 | 12910823.8765 | 14693904.4118 | 16080744.8282 | 17071345.1257 | 17665705.3041 | 17863825.3636 | 17665705.3041 | 17071345.1257 | 16080744.8282 | 14693904.4118 | 12910823.8765 | 10731503.2221 | 8155942.4488 | 5184141.5565 | 1816100.5453 | 0 | 0
Electrical / Critical Power (Div 26) |  | 248147784.9504 | 8 | 28 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1634490.3231 | 4689111.5826 | 7422193.7621 | 9833736.8618 | 11923740.8814 | 13692205.8211 | 15139131.6809 | 16264518.4607 | 17068366.1606 | 17550674.7805 | 17711444.3205 | 17550674.7805 | 17068366.1606 | 16264518.4607 | 15139131.6809 | 13692205.8211 | 11923740.8814 | 9833736.8618 | 7422193.7621 | 4689111.5826 | 1634490.3231 | 0 | 0
Openings (Div 08) |  | 13742209.9774 | 15 | 23 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471269.2036 | 1263001.4657 | 1828524.51 | 2167838.3366 | 2280942.9455 | 2167838.3366 | 1828524.51 | 1263001.4657 | 471269.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Finishes (Div 09) |  | 33189552 | 18 | 28 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773009.8512 | 2119543.1405 | 3166846.8099 | 3914920.8595 | 4363765.2893 | 4513380.0992 | 4363765.2893 | 3914920.8595 | 3166846.8099 | 2119543.1405 | 773009.8512 | 0 | 0
Specialties (Div 10) |  | 4010233.425 | 20 | 28 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137525.1517 | 368567.4067 | 533597.5888 | 632615.698 | 665621.7345 | 632615.698 | 533597.5888 | 368567.4067 | 137525.1517 | 0 | 0
Commissioning (Cx) | H312 (Cx) | 47367292.5 | 18 | 29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931995.3385 | 2576692.9948 | 3892451.1198 | 4879269.7135 | 5537148.776 | 5866088.3073 | 5866088.3073 | 5537148.776 | 4879269.7135 | 3892451.1198 | 2576692.9948 | 931995.3385 | 0
Security (Div 28) |  | 15750753.425 | 20 | 29 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441021.0959 | 1197057.2603 | 1764084.3836 | 2142102.4658 | 2331111.5069 | 2331111.5069 | 2142102.4658 | 1764084.3836 | 1197057.2603 | 441021.0959 | 0
IT Infrastructure (Div 27) | H277 (Div 27) | 60417387.7013 | 23 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2596059.6278 | 6844157.2005 | 9676222.249 | 11092254.7733 | 11092254.7733 | 9676222.249 | 6844157.2005 | 2596059.6278
General Conditions (Div 01) |  | 42983030.6039 | 1 | 30 | 30 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868 | 1432767.6868
Soft Costs / Pre-Con (SC) |  | 113098590 | 1 | 30 | 30 | 7296683.2258 | 7053460.4516 | 6810237.6774 | 6567014.9032 | 6323792.129 | 6080569.3548 | 5837346.5806 | 5594123.8065 | 5350901.0323 | 5107678.2581 | 4864455.4839 | 4621232.7097 | 4378009.9355 | 4134787.1613 | 3891564.3871 | 3648341.6129 | 3405118.8387 | 3161896.0645 | 2918673.2903 | 2675450.5161 | 2432227.7419 | 2189004.9677 | 1945782.1935 | 1702559.4194 | 1459336.6452 | 1216113.871 | 972891.0968 | 729668.3226 | 486445.5484 | 243222.7742
Masonry (Div 04) |  | 5656068 | 8 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243034.1719 | 640726.4531 | 905854.6406 | 1038418.7344 | 1038418.7344 | 905854.6406 | 640726.4531 | 243034.1719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wood / Plastics (Div 06) |  | 1233678.6 | 11 | 19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42307.2222 | 113383.3556 | 164152.0222 | 194613.2222 | 204766.9556 | 194613.2222 | 164152.0222 | 113383.3556 | 42307.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equipment (Div 11) |  | 1525590 | 20 | 28 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52317.9012 | 140211.9753 | 202993.4568 | 240662.3457 | 253218.642 | 240662.3457 | 202993.4568 | 140211.9753 | 52317.9012 | 0 | 0
Furnishings (Div 12) |  | 1217056.5 | 23 | 29 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67417.1239 | 173865.2143 | 237734.0685 | 259023.6866 | 237734.0685 | 173865.2143 | 67417.1239 | 0
Conveying (Div 14) |  | 4104292.5 | 18 | 28 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95592.0868 | 262107.3347 | 391619.1942 | 484127.6653 | 539632.7479 | 558134.4421 | 539632.7479 | 484127.6653 | 391619.1942 | 262107.3347 | 95592.0868 | 0 | 0
Integrated Automation (Div 25) |  | 13470732 | 15 | 29 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171627.104 | 482950.688 | 746378.336 | 961910.048 | 1129545.824 | 1249285.664 | 1321129.568 | 1345077.536 | 1321129.568 | 1249285.664 | 1129545.824 | 961910.048 | 746378.336 | 482950.688 | 171627.104 | 0
TOTAL |  | 1088341827.0674 |  |  |  | 9830083.9282 | 11387896.9978 | 13416438.1989 | 16621173.2217 | 19547508.6102 | 21124531.0719 | 21352240.6067 | 23508586.9416 | 28427724.4215 | 34619709.4053 | 41519972.0431 | 46861468.2319 | 49754053.3375 | 51186428.2042 | 51647878.6675 | 51492706.1635 | 51931098.7721 | 53897682.2595 | 55548583.034 | 55541420.166 | 54924276.9902 | 53235929.4402 | 52473910.9813 | 52376773.7281 | 49522619.8398 | 43577241.1495 | 34622850.1049 | 22279214.1347 | 11437081.3889 | 4674745.0267
CUMULATIVE | [5 empty] | 9830083.9282 | 21217980.926 | 34634419.1249 | 51255592.3466 | 70803100.9568 | 91927632.0287 | 113279872.6354 | 136788459.577 | 165216183.9985 | 199835893.4038 | 241355865.4469 | 288217333.6788 | 337971387.0162 | 389157815.2204 | 440805693.8879 | 492298400.0514 | 544229498.8236 | 598127181.083 | 653675764.1171 | 709217184.2831 | 764141461.2732 | 817377390.7135 | 869851301.6948 | 922228075.4229
% COMPLETE | [5 empty] | 0.9032% | 1.95% | 3.182% | 4.71% | 6.506% | 8.447% | 10.41% | 12.57% | 15.18% | 18.36% | 22.18% | 26.48% | 31.05% | 35.76% | 40.5% | 45.23% | 50.01% | 54.96% | 60.06% | 65.16% | 70.21% | 75.1% | 79.92% | 84.74%
QC: Schedule total = Construction Budget total |  | ✅ Tie
Note on A3: Phasing method (updated): construction trades use a cubic smoothstep S-curve weight w(k)=S(k/F)-S((k-1)/F), S(x)=3x^2-2x^3, applied within each trade's [Start Mo, End Mo] window. Weights sum to 1, so every division spreads to exactly its budget and the schedule total ties to the estimate. General Conditions level-loaded; Soft Costs front-loaded. Adjust Start/End Mo to reshape any trade.

## Cash Flow & EVM
CASH FLOW & EARNED VALUE (EVM)
Earned Value Management to the data date. Blue cells are inputs (Period Actual Cost & % Complete); metrics, the S-curve, and the dashed forecast-to-complete (cols K–L) update automatically as you advance the data date.
1 · EVM SCORECARD
Data Date (month #): | 0 | —
BAC — Budget at Completion | 1088341827.0674
PV — Planned Value to date | 0
EV — Earned Value to date | 0
AC — Actual Cost to date | 0
SV — Schedule Variance (EV−PV) | 0
CV — Cost Variance (EV−AC) | 0
SPI — Schedule Perf. Index | —
CPI — Cost Perf. Index | —
EAC — Estimate at Completion | 1088341827.0674
ETC — Estimate to Complete | 1088341827.0674
VAC — Variance at Completion | 0
TCPI — To-Complete Index | —
Schedule status: | ○ Not started
Cost status: | ○ Not started
PV curve ties to BAC: | ✅ Tie
BASELINE — Pre-construction. Budget at Completion $1,088.3M over a 30-month schedule. No actual cost or physical progress recorded yet — EVM metrics (SPI / CPI / EAC) populate automatically once actuals are entered and the Data Date (cell B5) is advanced.
2 · MONTHLY S-CURVE — Period AC & % Complete are inputs (enter Actual Cost in full $). All dollar figures display in $M.
Month | Month-End | Period PV ($M) | Cum PV ($M) | Period AC ($M) | Cum AC ($M) | % Complete | Cum EV ($M) | SPI | CPI | Fcst Cum AC ($M) | Fcst Cum EV ($M)
1 | 2026-05-31 | 9830083.9282 | 9830083.9282 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
2 | 2026-06-30 | 11387896.9978 | 21217980.926 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
3 | 2026-07-31 | 13416438.1989 | 34634419.1249 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
4 | 2026-08-31 | 16621173.2217 | 51255592.3466 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
5 | 2026-09-30 | 19547508.6102 | 70803100.9568 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
6 | 2026-10-31 | 21124531.0719 | 91927632.0287 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
7 | 2026-11-30 | 21352240.6067 | 113279872.6354 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
8 | 2026-12-31 | 23508586.9416 | 136788459.577 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
9 | 2027-01-31 | 28427724.4215 | 165216183.9985 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
10 | 2027-02-28 | 34619709.4053 | 199835893.4038 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
11 | 2027-03-31 | 41519972.0431 | 241355865.4469 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
12 | 2027-04-30 | 46861468.2319 | 288217333.6788 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
13 | 2027-05-31 | 49754053.3375 | 337971387.0162 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
14 | 2027-06-30 | 51186428.2042 | 389157815.2204 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
15 | 2027-07-31 | 51647878.6675 | 440805693.8879 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
16 | 2027-08-31 | 51492706.1635 | 492298400.0514 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
17 | 2027-09-30 | 51931098.7721 | 544229498.8236 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
18 | 2027-10-31 | 53897682.2595 | 598127181.083 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
19 | 2027-11-30 | 55548583.034 | 653675764.1171 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
20 | 2027-12-31 | 55541420.166 | 709217184.2831 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
21 | 2028-01-31 | 54924276.9902 | 764141461.2732 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
22 | 2028-02-29 | 53235929.4402 | 817377390.7135 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
23 | 2028-03-31 | 52473910.9813 | 869851301.6948 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
24 | 2028-04-30 | 52376773.7281 | 922228075.4229 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
25 | 2028-05-31 | 49522619.8398 | 971750695.2627 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
26 | 2028-06-30 | 43577241.1495 | 1015327936.4122 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
27 | 2028-07-31 | 34622850.1049 | 1049950786.5171 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
28 | 2028-08-31 | 22279214.1347 | 1072230000.6517 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
29 | 2028-09-30 | 11437081.3889 | 1083667082.0407 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
30 | 2028-10-31 | 4674745.0267 | 1088341827.0674 |  | #N/A |  | #N/A |  |  | #N/A | #N/A
Formulas:
Month-End = EOMONTH('Construction Budget'!$F3,[Month]-1)
Note on B5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: REQUIRED INPUT — Data Date (month #). Enter the month being closed, integer 0–24 (0 = baseline/not started). Source: project calendar/cutoff, set monthly by PM. Drives the entire scorecard and the S-curve cutoff.
Note on B6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SOURCE LINK (live): ='Campus Rollup'!H16 = Budget at Completion. Auto-ties to the PV curve total (D47). No manual entry.
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SOURCE LINK (live): Period PV S-curve ='Draw Schedule'!G32:AD32 across C24:C47. Foots to BAC. No manual entry.
Note on E24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: REQUIRED INPUT — Period Actual Cost (E24:E47). Enter cost incurred THAT month in full dollars (e.g. 24500000). Source: contractor pay apps (AIA G702/G703) / cost ledger / AP actuals, monthly from Cost Control. Cumulated in col F; unlocks AC, CV, CPI, EAC, ETC, VAC, TCPI.
Note on G24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: REQUIRED INPUT — % Complete (G24:G47). Enter cumulative PHYSICAL % complete at the data date (e.g. 12.5%). Source: monthly progress assessment / earned schedule from Superintendent/PM. EV = % × BAC; unlocks EV, SV, SPI, CV. Keep physical, not cost-based.

## Client Proposal
↓ FIRM / COMPANY NAME — enter your firm name here to fill every blank in this proposal (letterhead, cover letter, signature). Leave blank to keep them blank.
↓ Street address
↓ City, State ZIP
| 2026-06-15 |  |  |  | ↓ Phone
Attention: Project Development Team
Data Center Template, Northern Virginia
Loudoun County, VA
RE: Design Development (Class 3) Cost Estimate — Data Center Template, Northern Virginia
Proposal No. TT-DC-2026-0615
Dear Members of the Project Development Team,
is pleased to submit the enclosed Design Development (Class 3) cost estimate for Data Center Template, Northern Virginia, an 800,000-square-foot, 90 MW (critical IT) Tier III data center campus in Loudoun County, Virginia.
The enclosed proposal presents a total campus estimate of $1,105,891,827, organized across twelve scope categories and detailed to the CSI MasterFormat division level in the accompanying Schedule of Values. Pricing reflects current market conditions, with contingency embedded in every line item and escalation carried to the anticipated construction midpoint.
The estimate excludes owner-furnished IT equipment, financing and carrying costs, and land acquisition. Full assumptions, qualifications, terms, and exclusions are set out in the sections and appendices that follow. This proposal is valid for thirty (30) days from the date above.
We appreciate the opportunity to support this project and welcome the chance to review the estimate with your team at your convenience. Please do not hesitate to contact us with any questions.
Respectfully submitted,
Prepared by: ______________________________
Cost Management & Estimating
TABLE OF CONTENTS
| Executive Summary |  |  | 3
| Investment Highlights |  |  | 3
| Scope of Work & Pricing Summary |  |  | 4
| Terms & Conditions |  |  | 5
| Exclusions |  |  | 5
| Acceptance & Signatures |  |  | 6
| Appendix A — Schedule of Values |  |  | 7
| Appendix B — Basis of Estimate |  |  | 8
DATA CENTER COST ESTIMATE — PROPOSAL
| Project Name: | Data Center Template, Northern Virginia
| Project Location: | Loudoun County, VA
| Owner / Client: | Confidential Hyperscaler
| Facility Size (SF): | 800,000 sf
| IT Power Capacity: | 90 MW
| Tier Rating: | Tier III
| Proposal Date: | 2026-06-15
| Valid Through: | 2026-07-15
| Proposal No.: | TT-DC-2026-0615
Prepared By:
Reviewed By:
EXECUTIVE SUMMARY
is pleased to submit this Design Development (Class 3) cost estimate for Data Center Template, Northern Virginia — an 800,000 SF, 90 MW (critical IT) Tier III data center campus in Loudoun County, Virginia. The projected all-in capital cost is summarized by the capital-efficiency metrics in the Investment Highlights below, broken down across twelve scope categories in the Scope & Pricing Summary, and detailed to the CSI-division level in the Schedule of Values (Appendix A). Pricing reflects current market rates, with contingency embedded in every line item and escalation carried to the anticipated construction midpoint. The estimate excludes owner-furnished IT equipment, financing and carrying costs, and land. Full assumptions and qualifications are set out in the Basis of Estimate (Appendix B), Terms & Conditions, and Exclusions.
INVESTMENT HIGHLIGHTS — CAPITAL EFFICIENCY
| Total Capital Investment | 1105891827.0674 | All-in: construction + owner allowances
| Cost per MW (IT) | 12287686.9674 | Capital intensity per MW of critical IT load
| Cost per Watt (IT) | 12.2877 | Benchmark range for hyperscale: $9–14 / W
| Cost per Gross SF | 1382.3648 | Across 800,000 gross SF of facility
| IT Power Capacity | 90 | Critical IT load (N), Tier III concurrent
| Embedded Contingency | 10% | Carried within every line item, not separate
| Estimate Class | Class 3 (DD) | AACE maturity (Design Development)
| Resiliency / Efficiency | Tier III | Concurrently maintainable; PUE ~1.3
SCOPE OF WORK & PRICING SUMMARY
# | Description | Amount | % of Total
A | Civil & Site Work | 98585143.8392 | 9.058%
Earthwork, grading, paving, utilities, fencing, stormwater, security perimeter
B | Structural & Building Shell | 133100047.6019 | 12.23%
Foundations, structural steel, concrete, masonry, roofing, exterior walls, carpentry, loading docks
C | Electrical — Critical Power | 261618516.9504 | 24.04%
Utility switchgear, transformers, generators, UPS, STS, PDUs, busway, grounding, and integrated automation / controls
D | Mechanical — Cooling Systems | 226484248.0019 | 20.81%
Chillers, cooling towers, CRAHs, CRACs, piping, hot/cold aisle containment, economizer systems, controls
E | Fire & Life Safety | 22577593.5 | 2.074%
Clean agent suppression (FM-200/Novec), VESDA detection, pre-action sprinklers, smoke evacuation, fire alarm/mass notification
F | Building Systems & Finishes | 44046724.425 | 4.047%
Interior finishes, raised floor, doors/openings, equipment, furnishings, conveying/elevators, signage, specialties
G | IT Infrastructure & Cabling | 60417387.7013 | 5.551%
Structured cabling, fiber backbone, cable tray, ladder rack, cabinets/racks, overhead busway, BMS/DCIM integration
H | Security & Monitoring | 15750753.425 | 1.447%
Access control, CCTV, mantraps, bollards, perimeter intrusion detection, NOC/SOC buildout, BMS integration
I | Commissioning & Testing | 47367292.5 | 4.352%
Levels 1–5 commissioning, IST, factory witness testing, performance verification, documentation turnover
J | Plumbing Systems | 22312498.5188 | 2.05%
Domestic water, sanitary waste, condensate drain, make-up water, acid neutralization, compressed air, backflow prevention
K | General Conditions & Requirements | 42983030.6039 | 3.949%
Project management, temporary facilities, QA/QC, permits, bonds, insurance, closeout, waste management
L | Soft Costs / Pre-Construction | 113098590 | 10.39%
A/E design fees, permitting, third-party CxA, Uptime certification, LEED certification, BIM, testing/inspection, owner's rep
| SUBTOTAL — ALL DIVISIONS (CAMPUS) | 1088341827.0674 | 100%
| CONTINGENCY ALLOWANCE | 0 | 10%
| ACCEPTED ALTERNATES (Net Add/Deduct) | 0 | 0%
| ESTIMATE BASIS NOTES | Class 3 (DD) estimate; see Basis of Estimate tab
| OWNER ALLOWANCES (carried in budget) | 17550000 | 1.613%
| TOTAL CAMPUS ESTIMATE | 1105891827.0674
Includes shared campus infrastructure and embedded contingency. Excludes owner-furnished IT equipment, financing/carrying costs, and land acquisition.
TERMS & CONDITIONS
1. This proposal is valid for thirty (30) calendar days from the Proposal Date shown above.
2. Payment schedule: 10% deposit upon execution, progress draws per AIA G702/G703, 10% retention released upon substantial completion, successful IST, and punch list close-out.
3. Work not expressly included shall require a written Change Order signed by both parties prior to commencement. Change Orders may adjust the contract price and/or schedule.
4. Owner is responsible for utility service to the property line, all utility connection fees, AHJ permits beyond those listed, and temporary power during construction.
5. Contractor shall maintain general liability ($2M per occurrence / $5M aggregate), professional liability ($5M), and workers' compensation insurance for the duration of the project.
6. All work shall conform to applicable local, state, and federal building codes; NFPA 75/76; Uptime Institute Tier Standards; and manufacturer installation specifications.
7. Warranty: Two (2) year workmanship warranty from substantial completion. All critical infrastructure (UPS, generators, chillers, switchgear) carry manufacturer warranties as specified.
8. Commissioning: Contractor shall perform Levels 1–5 commissioning per Uptime Institute standards, including Integrated Systems Testing (IST). Owner-directed commissioning agent (CxA) costs are excluded unless listed.
EXCLUSIONS (unless specifically included above)
• IT equipment (servers, networking, storage) — this proposal covers infrastructure only
• Furniture, fixtures, and equipment (FF&E) for office/NOC areas not specifically listed
• Hazardous material testing or remediation (asbestos, lead, contaminated soil)
• Architectural design revisions after construction document approval; permit re-submittals due to owner changes
• Unforeseen subsurface conditions including rock removal, dewatering, or contaminated soil remediation
• Owner-furnished commissioning agent (CxA) fees; third-party Uptime Institute Tier certification audit fees
• Bid, performance, or payment bonds unless expressly required
• Seismic bracing beyond code minimum (unless Tier IV fault-tolerant design is specified)
ACCEPTANCE
By signing below, Owner acknowledges review and acceptance of the scope of work, pricing, terms, conditions, and exclusions set forth herein, and authorizes Contractor to proceed.
| CONTRACTOR | OWNER / CLIENT
| Signature: | Signature:
| Print Name: | Print Name:
| Date: | Date:
APPENDIX A — DETAILED SCHEDULE OF VALUES
Cost breakdown by CSI MasterFormat division — amounts pulled live from the detailed construction estimate (24 divisions, 747 priced line items).
Div | CSI Division | Amount | % of Subtotal
31 | Earthwork & Site Preparation | 25614732 | 2.354%
32 | Exterior Improvements | 9371809.4642 | 0.8611%
33 | Utilities (Site) | 63598602.375 | 5.844%
3 | Concrete | 33466040.3876 | 3.075%
5 | Metals / Structural Steel | 40836399.762 | 3.752%
7 | Thermal & Moisture Protection | 38165650.875 | 3.507%
22 | Plumbing | 22312498.5188 | 2.05%
21 | Fire Suppression | 22577593.5 | 2.074%
23 | HVAC / Cooling Systems | 226484248.0019 | 20.81%
26 | Electrical / Critical Power | 248147784.9504 | 22.8%
8 | Openings (Doors, Frames, Louvers) | 13742209.9774 | 1.263%
9 | Finishes | 33189552 | 3.05%
10 | Specialties | 4010233.425 | 0.3685%
27 | Communications / IT Infrastructure | 60417387.7013 | 5.551%
28 | Electronic Safety & Security | 15750753.425 | 1.447%
4 | Masonry | 5656068 | 0.5197%
6 | Wood, Plastics & Composites | 1233678.6 | 0.1134%
11 | Equipment | 1525590 | 0.1402%
12 | Furnishings | 1217056.5 | 0.1118%
14 | Conveying Equipment | 4104292.5 | 0.3771%
25 | Integrated Automation (BMS / DCIM) | 13470732 | 1.238%
CX | Commissioning & Testing (L1–L5 / IST) | 47367292.5 | 4.352%
1 | General Conditions & Requirements | 42983030.6039 | 3.949%
SC | Soft Costs / Pre-Construction | 113098590 | 10.39%
| SUBTOTAL — ALL DIVISIONS (CAMPUS) | 1088341827.0674 | 100%
APPENDIX B — BASIS OF ESTIMATE & KEY ASSUMPTIONS
Key parameters underlying this estimate — all values linked live to the cost model.
| Estimate Class | Class 3 (DD)
| Estimate Accuracy Range | −10% / +15% (AACE Class 3)
| Pricing Basis | Unit Cost Database — Low tier
| Escalation to Construction Midpoint | 3.5%
| Location Factor | 1
| Embedded Contingency | 10%
| Estimate Date | 2026-05-01
| Currency | USD ($)
| Gross Building Area | 800000
| IT Critical Load (N) | 90
| Resiliency Tier | Tier III
| CSI Divisions Priced | 24
| Priced Line Items | 747
Methodology & Inclusions
• Quantities derived from Design Development documents and digital takeoff; unit rates sourced from the project Unit Cost Database.
• Every line item carries embedded contingency; no separate contingency line is added to the subtotal.
• Pricing assumes competitive lump-sum procurement, prevailing-wage labor, and a single continuous construction program.
• Excludes owner-furnished IT equipment, financing and carrying costs, and land acquisition (see Exclusions).
• Escalation carried to the anticipated construction midpoint; re-pricing is recommended at each subsequent design milestone.
Note on C129: Kevin: Set to 0 — contingency is already included in every Construction Budget line item via the (1+$H$7) factor in column H. Adding another 10% here double-counted by ~$178M.

## Carbon & Sustainability
CARBON & SUSTAINABILITY ESTIMATE
Embodied (cradle-to-completion) + operational carbon alongside capex. Yellow cells are inputs. Factors are early-stage planning values — refine with an LCA.
LIFECYCLE CARBON 0.68M tCO₂e • 0.85 tCO₂e/SF • 58% embodied / 42% operational • $1,592 capex/tCO₂e
1 · INPUTS & REFERENCES |  |  |  | ACTIVE SCENARIO
Gross building area (GBA) | 800000 | SF — from Campus Rollup |  | Efficient
IT load | 90 | MW — from Campus Rollup |  | ▼ drives PUE · grid · PPA · WUE
PUE | 1.2 | facility kW per IT kW
Average utilisation | 80% | of IT capacity
Operating life (assessment period) | 15 | years
Grid carbon intensity | 0.25 | tCO₂e per MWh
Renewable PPA coverage | 90% | of energy carbon-free
2 · EMBODIED CARBON (modules A1–A5)
Element | Intensity (tCO₂e/SF) | Embodied (tCO₂e) | % of embodied |  | Embodied | 400000
Substructure & superstructure | 0.3 | 240000 | 60% |  | Operational (life) | 283824
Envelope & architecture | 0.08 | 64000 | 16%
MEP systems & equipment | 0.12 | 96000 | 24%
Total embodied carbon |  | 400000
3 · OPERATIONAL CARBON
Facility load | 108 | MW = IT × PUE
Annual energy use | 756864 | MWh / yr = facility × 8760 × util.
Effective grid intensity | 0.025 | tCO₂e/MWh after renewable PPA
Annual operational carbon | 18921.6 | tCO₂e / yr
Lifetime operational carbon | 283824 | tCO₂e over assessment period
4 · LIFECYCLE SUMMARY & CARBON–COST METRICS
Total lifecycle carbon | 683824 | tCO₂e = embodied + lifetime operational
Embodied as % of lifecycle | 58.49% | the rest is operational
Lifecycle carbon per MW | 7598.0444 | tCO₂e / IT MW
Lifecycle carbon per SF | 0.85478 | tCO₂e / SF
Capex per lifecycle tCO₂e | 1591.5525 | $ capex per tCO₂e
Embodied carbon per $ capex | 0.36753 | kgCO₂e per $ capex
5 · DECARBONISATION LEVERS — QUANTIFIED SCENARIO (planning)
Lever | Target | Carbon base (tCO₂e) | Reduction % | Carbon saved (tCO₂e)
Low-carbon concrete (GGBS / fly-ash mix) | Embodied | 240000 | 12.5% | 30000
Renewable PPA → 90% coverage | Operational | 2152332 | 80% | 1721865.6
Waste-heat reuse / district loop | Operational | 2152332 | 4.5% | 96854.94
Lower design PUE (1.30 → 1.20) | Operational | 2152332 | 8% | 172186.56
Low-GWP refrigerants & SF₆-free gear | Embodied | 400000 | 1.5% | 6000
6 · COMBINED DECARBONISATION SCENARIO
Base lifecycle carbon | 2552332 | embodied + lifetime operational |  |  |  | Embodied | Operational
Embodied after levers | 364000 | concrete + low-GWP levers |  |  | Base case | 400000 | 2152332
Operational after levers | 378207.779 | PPA, waste-heat & PUE compounded |  |  | With levers | 364000 | 378207.779
Lifecycle carbon WITH levers | 742207.779 | post-lever total
Reduction vs base | 70.92% | lifecycle carbon avoided
New lifecycle intensity | 0.92776 | tCO₂e / SF (was 3.19)
Net cost premium (% of capex) | 1% | planning estimate — refine with VE pricing
Net cost premium ($) | 10883418.2707 | on total project capex
Implied abatement cost | 6.0125 | $ per tCO₂e abated
POTENTIAL WITH LEVERS 0.74M tCO₂e • −71% vs base • 0.93 tCO₂e/SF • $6.01/tCO₂e abated
7 · WATER CONSUMPTION (operational)
Water usage effectiveness (WUE) | 0.2 | L per kWh IT energy • evaporative 1.4–2.2; hybrid ~0.5; closed-loop ≤0.2
Annual IT energy | 630720 | MWh / yr (IT load × 8760 × util.)
Annual water withdrawal | 126144 | m³ / yr (WUE × IT MWh)
Annual water withdrawal | 126.144 | megalitres / yr
Lifetime water withdrawal | 1892160 | m³ over assessment period
Water intensity per MW | 1401.6 | m³ / IT MW / yr
Water intensity per SF | 157.68 | L / SF / yr
WATER 126 ML/yr • 1,892 ML lifetime • 158 L/SF/yr • WUE 0.20 L/kWh
8 · SCENARIO MANAGER & COMPARISON
Pick Active Scenario (top of Inputs) to drive the live model. Columns below define each scenario — edit the yellow cells; Custom is fully user-defined. Note the water–energy trade-off (evaporative cooling lowers PUE but raises WUE).
Driver / Outcome | Efficient | Base | Conservative | Custom |  | Efficient | Base | Conservative | Custom
DRIVERS |  |  |  |  | Lifecycle carbon (tCO₂e) | 683824 | 2552332 | 5338537.6 | 2552332
PUE | 1.2 | 1.3 | 1.45 | 1.3 | Annual water (ML) | 126.144 | 1135.296 | 1387.584 | 1135.296
Grid intensity (tCO₂e/MWh) | 0.25 | 0.35 | 0.45 | 0.35
Renewable PPA coverage | 90% | 50% | 20% | 50%
WUE (L/kWh) | 0.2 | 1.8 | 2.2 | 1.8
CARBON OUTCOMES
Annual operational carbon (tCO₂e/yr) | 18921.6 | 143488.8 | 329235.84 | 143488.8
Lifecycle carbon (tCO₂e) | 683824 | 2552332 | 5338537.6 | 2552332
Lifecycle intensity (tCO₂e/SF) | 0.85478 | 3.1904 | 6.6732 | 3.1904
Embodied % of lifecycle | 58.49% | 15.67% | 7.493% | 15.67%
WATER OUTCOMES
Annual water (ML/yr) | 126.144 | 1135.296 | 1387.584 | 1135.296
Lifetime water (ML) | 1892.16 | 17029.44 | 20813.76 | 17029.44
Water intensity (L/SF/yr) | 157.68 | 1419.12 | 1734.48 | 1419.12
Note on A37: Kevin: Embodied lever. Applies to substructure & superstructure embodied carbon. Source range: −10–15% structural; cost +1–2% concrete.
Note on A38: Kevin: Operational lever. −80% operational vs current 50% PPA; market-neutral cost.
Note on A39: Kevin: Operational lever. −3–6% operational; cost +1–3% MEP.
Note on A40: Kevin: Operational lever. −8% operational; cost +2–4% cooling.
Note on A41: Kevin: Embodied lever. −1–2% embodied; cost neutral–small.
Note on A54: Kevin: Anchored to the BASE scenario (not the Active Scenario dropdown). This shows the standalone potential of the decarbonization levers measured from a standard build, so it is NOT directly comparable to the active-scenario lifecycle headline (A3). The Efficient scenario already embeds the PPA/PUE improvements these levers represent, so the two views are intentionally independent to avoid double-counting.
Note on B7: Kevin: Driven by Active Scenario (E5). Edit values in the Section 8 scenario table, or pick Custom and edit column E.
Note on B10: Kevin: Driven by Active Scenario (E5).
Note on B11: Kevin: Driven by Active Scenario (E5).
Note on B57: Kevin: Driven by Active Scenario (E5).
Note on C38: Kevin: Base-case lifetime operational carbon (anchored to Base scenario, independent of the Active Scenario dropdown).

## Reference Models
REFERENCE MODELS — DATA CENTER COST BENCHMARKING SOURCES
External cost models, benchmarks, and templates used to calibrate this estimate. Refer to these when validating assumptions, sourcing unit costs, or extending the model into operating-cost / lifecycle territory.
# | Source | Type | Coverage | Access | Best Used For | Link / Reference
1 | RSMeans Computer Data Center Cost Model | CSI line-item cost database | 22,500 SF baseline data center; structural, MEP, envelope by system; union & open-shop labor | Paid (30-day free trial) | Most credible source for divisional-level construction cost benchmarking; calibrating Construction Budget unit costs | rsmeans.com
2 | TechTarget Data Center Cost Calculator | Downloadable Excel — CapEx + OpEx | Install year + 8 years operations: land, utilities, hall buildout, cooling, security, depreciation | Free download | Lifecycle TCO framing; what to include in OpEx beyond pure construction | techtarget.com
3 | Adventures in CRE — Data Center Development Model | Excel — Development pro forma | Draw schedule, construction phasing, tenant absorption, operating cash flow, refi/exit valuation; PUE-linked utility modeling | Free / paid tiers | Bridging project controls to CRE finance; structuring construction & mezz loan draws; refi scenarios. Updated April 2026. | adventuresincre.com
4 | Scribd Data Center Facility Budget Tool | Excel template | 1,000 SF facility, 8-year capex + opex, building/site/systems | Free (Scribd account) | Quick reference for small-facility cost structure; not directly applicable at hyperscale but useful for sanity-checking line-item ratios | scribd.com
5 | HP Labs Data Center Cost Model (Patel & Shah) | Academic — parametric formulas | Space, power, cooling cost as functions of redundancy, PUE, occupancy ratio | Free (ResearchGate) | Operational TCO framework; understanding cost drivers and sensitivities; not a ready-to-use template | researchgate.net
6 | Smartsheet / ProjectManager.com Construction Estimate Templates | Generic construction templates | Pre-con / construction / post-con phases; labor + material breakdowns | Free | Schedule / phase template structure; not data-center specific but adaptable | smartsheet.com / projectmanager.com
RECOMMENDED USE FOR THIS PROJECT
• RSMeans — anchor unit prices on Construction Budget when refining estimate from Class 3 (DD) toward Class 2 (CD).
• A.CRE model — reference structure for Draw Schedule tab; calibrate construction phasing curves and integrate with project finance.
• TechTarget + HP Labs — reference structure for TCO 8-Year tab; PUE / utility / maintenance assumptions.
• Benchmark Library tab in this workbook holds 10 comparable Tier III hyperscale projects; use that for $/SF and $/MW comps before going external.

## _ChartData (hidden)
Milestone | Estimate ($M) |  | Scope | Amount ($M) | Dashboard chart data (relocated) — do not edit |  | Milestone | Completion
Concept | 981.249 |  | CSA | 275.7319 | All other trades | 70082423.8916 | Site Opening / Go-Live | 2029-02-24
SD | 1025.218 |  | MEP | 609.161 | Concrete | 33466040.3876 | Certificate of Occupancy | 2029-02-09
DD | 1062.2216 |  | Cx / GC / Soft | 203.4489 | Earthwork | 25614732 | Substantial Completion | 2029-01-20
CD | 1088.3418 |  |  |  | Fire Suppression | 22577593.5 | Commissioning Complete | 2029-01-15
GMP | 1110.1087 |  |  |  | Plumbing | 22312498.5188 | Mechanical Water-On | 2028-09-22
Awarded | #N/A |  |  |  | Finishes | 33189552 | Power-On / Energization | 2028-08-23
[5 empty] | Thermal & Moisture | 38165650.875 | Building Weather-Tight | 2027-10-13
[5 empty] | Structural Steel | 40836399.762 | Building Dried-In | 2027-08-29
[5 empty] | Commissioning | 47367292.5 | All Equipment On Site | 2026-10-28
[5 empty] | General Conditions | 42983030.6039 | Construction Start (NTP) | 2026-05-01
[5 empty] | Communications / IT | 60417387.7013 | Long-Lead Release (PO) | 2026-03-02
[5 empty] | Utilities | 63598602.375 | Design Complete / IFC | 2026-05-31
[5 empty] | Soft Costs / Pre-Con | 113098590 | Building Permit Issuance | 2026-05-01
[5 empty] | Electrical / Critical Power | 248147784.9504 | Land Acquisition / Closing | 2025-07-20
[5 empty] | HVAC / Cooling | 226484248.0019 | Site Selection Decision | 2025-06-05
[5 empty] | Lowest comparable | 9.8
[5 empty] | Industry median | 11.4
[5 empty] | Highest comparable | 17.8
[5 empty] | This project | 12.0927
[5 empty] | Current (Base) | 1088341827.0674
[5 empty] | Hyperscale (Hybrid) | 1758235505.1988
[5 empty] | Air-Cooled | 1676758035.8992
[5 empty] | AI / HPC (Liquid) | 3019287023.6146
[5 empty] | Enterprise | 1855155273.8992
[5 empty] | Colocation | 1626646451.8992
[5 empty] | Edge | 1058453752.0167
[5 empty] | Construction | 1088.3418
[5 empty] | Land | 80
[5 empty] | Utility interconnect | 117
[5 empty] | Owner PM & soft costs | 71.5337
[5 empty] | Financing (IDC) | 83.9567
[5 empty] | Owner's contingency | 72.0416
[5 empty] | Yr 1 | 76.633
[5 empty] | Yr 2 | 135.77
[5 empty] | Yr 3 | 167.9438
[5 empty] | Yr 4 | 180.2181
[5 empty] | Yr 5 | 185.6246
[5 empty] | Yr 6 | 191.1933
[5 empty] | Yr 7 | 196.9291
[5 empty] | Yr 8 | 202.837
[5 empty] | Senior debt | 907.7243
[5 empty] | Sponsor equity | 605.1495
[5 empty] | Unlevered IRR | 17.44%
[5 empty] | Levered equity IRR | 26.65%
PHASED BUILD-OUT CHART SOURCE — do not edit
Phase | Cumulative capex ($B) | Blended $/MW ($M)
Phase 1a | 0.53219 | 17.7395
Phase 1b | 1.0883 | 12.0927
Phase 2 | 1.3762 | 11.4679
Phase 3 | 1.674 | 11.1603
Phase 4 | 1.9823 | 11.013